## Dashboard (hidden)
WATER TESTING QUALITY DASHBOARD
FILTERS
Record Type: | PQ1-2/OCL
Water Type: | PRW
Location: | AFTER RO SYSTEM NO.12 SV15
Result: | FAILED
METRICS
Total Tests | 908 | Passed | 883
Failed | 25 | Pass Rate | 97.2%
Record Type | Passed | Failed
PQ1-2/OCL | 67 | 0
PQ1-2/OLD | 81 | 0
Routine | 735 | 25
Water Type | Passed | Failed
PRW | 73 | 24
PW | 782 | 1
RO water | 28 | 0
Location | Passed | Failed
AFTER RO SYSTEM NO.12 SV14 | 15 | 3
AFTER RO SYSTEM NO.12 SV15 | 8 | 2
ALCOHOL STORAGE | 2 | 0
AUTOCLAVE | 4 | 0
After Cartridge filter 5 µm (B10) | 17 | 12
After Cartridge filter 5 µm (B12) | 1 | 0
After Cartridge filter 5 µm (B16) | 1 | 1
After Chlorine circulation tank (B10) | 25 | 0
After Chlorine circulation tank (B16) | 2 | 0
After EDI (B10) | 24 | 0
After EDI (B12) | 1 | 0
After EDI (B16) | 2 | 0
After Pump | 1 | 0
After RO (Before EDI) (B10) | 26 | 0
After RO (Before EDI) (B12) | 1 | 0
Month | Passed | Failed
2025-01-01 | 62 | 7
2025-02-01 | 73 | 4
2025-03-01 | 52 | 1
2025-04-01 | 71 | 2
2025-05-01 | 42 | 1
2025-06-01 | 71 | 4
2025-07-01 | 61 | 3
2025-08-01 | 58 | 3
2025-09-01 | 60 | 0
2025-10-01 | 61 | 0
2025-11-01 | 63 | 0
2025-12-01 | 209 | 0
Status | Count
Passed | 883
Failed | 25
PERFORMANCE BY RECORD TYPE
Record Type | Total | Passed | Pass %
PQ1-2/OCL | 67 | 67 | 100
PQ1-2/OLD | 81 | 81 | 100
Routine | 760 | 735 | 96.7
TOP LOCATIONS BY PASS RATE
Location | Total | Passed | Pass %
WET GRANULATION-5 | 11 | 11 | 100
WET GRANULATION-2 | 25 | 25 | 100
TOOL WASHING | 12 | 12 | 100
WASHING | 56 | 56 | 100
CIP SKID-1 FOR BIN WASHING-1 | 13 | 13 | 100
CIP SKID-2 FOR BIN WASHING-1 | 13 | 13 | 100
BINDER PREPARATION | 12 | 12 | 100
IPQC-2 | 12 | 12 | 100
After Chlorine circulation tank (B10) | 25 | 25 | 100
After RO (Before EDI) (B10) | 26 | 26 | 100
WATER TYPE PERFORMANCE
Water Type | Total | Passed | Pass %
RO water | 28 | 28 | 100
PW | 783 | 782 | 99.9
PRW | 97 | 73 | 75.3

## prw-pw
samplingDate | samplingPoint | samplingTag | recordStatus | worksheet No. | worksheetCreate | noLocation | building | location | waterType | performedDate | determinedDate | result1 | result2 | resultAvg | qualityEvent | comment | criteria | statusResult | Exclude | status | syncStatus
2026-05-19 | OSD28 | DV116.15 | Speacial | WT-26-0070 | TRUE | 10-3-104 | Building 10 | BINDER PREPARATION | PW | 2026-05-20 | 2026-05-23 | 17 | 7 | 12 | เก็บเพิ่มจาก oos PW-M-2-26-001 |  | 100 | PASSED | FALSE |  | synced
2026-05-22 | GOSD01 | VB-05(10) | PQ3-Week3 | WT-26-0071 | TRUE | WATER SYSTEM (B10) | Building 10 | After Chlorine circulation tank (B10) | PRW | 2026-05-23 | 2026-05-31 | 0 | 0 | 0 |  |  | 500 | PASSED |  |  | synced
2026-05-22 | GOSD03 | V50-61(10) | PQ3-Week3 | WT-26-0071 | TRUE | WATER SYSTEM (B10) | Building 10 | After Cartridge filter 5 µm (B10) | PRW | 2026-05-23 | 2026-05-31 | 0 | 0 | 0 |  |  | 500 | PASSED |  |  | synced
2026-05-22 | GOSD04 | V50-11C(10) | PQ3-Week3 | WT-26-0071 | TRUE | WATER SYSTEM (B10) | Building 10 | After RO (Before EDI) (B10) | RO water | 2026-05-23 | 2026-05-31 | 0 | 0 | 0 |  |  | 500 | PASSED |  |  | synced
2026-05-22 | GOSD05 | V50-39(10) | PQ3-Week3 | WT-26-0071 | TRUE | WATER SYSTEM (B10) | Building 10 | After EDI (B10) | PW | 2026-05-23 | 2026-05-31 | 0 | 0 | 0 |  |  | 100 | PASSED |  |  | synced
2026-05-22 | GOSD06 | SV113.01 | PQ3-Week3 | WT-26-0071 | TRUE | WATER SYSTEM (B10) | Building 10 | After Storage tank (B10) | PW | 2026-05-23 | 2026-05-31 | 0 | 0 | 0 |  |  | 100 | PASSED |  |  | synced
2026-05-22 | GOSD07 | SV115.02 | PQ3-Week3 | WT-26-0071 | TRUE | WATER SYSTEM (B10) | Building 10 | After UV (B10) | PW | 2026-05-23 | 2026-05-31 | 0 | 0 | 0 |  |  | 100 | PASSED |  |  | synced
2026-05-22 | GOSD08 | SV117.01 | PQ3-Week3 | WT-26-0071 | TRUE | WATER SYSTEM (B10) | Building 10 | Return loop (B10) | PW | 2026-05-23 | 2026-05-31 | 0 | 0 | 0 |  |  | 100 | PASSED |  |  | synced
2026-05-22 | OSD13 | DV116.25 | PQ3-Week3 | WT-26-0071 | TRUE | 10-3-171 | Building 10 | TOOL WASHING-P | PW | 2026-05-23 | 2026-05-31 | 0 | 0 | 0 |  |  | 100 | PASSED |  |  | synced
2026-05-22 | OSD14 | DV116.24 | PQ3-Week3 | WT-26-0071 | TRUE | 10-3-163 | Building 10 | WET GRANULATION 1-P |  | 2026-05-23 | 2026-05-31 | 0 | 0 | 0 |  |  | 100 | PASSED |  |  | synced
2026-05-22 | OSD15 | DV116.23 | PQ3-Week3 | WT-26-0071 | TRUE | 10-3-159 | Building 10 | BINDER PREPARATION-P | PW | 2026-05-23 | 2026-05-31 | 0 | 0 | 0 |  |  | 100 | PASSED |  |  | synced
2026-05-22 | OSD16 | DV116.21 | PQ3-Week3 | WT-26-0071 | TRUE | 10-3-152 | Building 10 | WASHING-P | PW | 2026-05-23 | 2026-05-31 | 0 | 0 | 0 |  |  | 100 | PASSED |  |  | synced
2026-05-22 | OSD17 | DV116.22 | PQ3-Week3 | WT-26-0071 | TRUE | 10-3-152 | Building 10 | WASHING-P | PW | 2026-05-23 | 2026-05-31 | 0 | 0 | 0 |  |  | 100 | PASSED |  |  | synced
2026-05-22 | OSD18 | SV116.13 | PQ3-Week3 | WT-26-0071 | TRUE | 10-3-152 | Building 10 | WASHING-P | PW | 2026-05-23 | 2026-05-31 | 0 | 0 | 0 |  |  | 100 | PASSED |  |  | synced
2026-05-22 | OSD19 | DV116.20 | PQ3-Week3 | WT-26-0071 | TRUE | 10-3-149 | Building 10 | IPQC-1-P | PW | 2026-05-23 | 2026-05-31 | 0 | 0 | 0 |  |  | 100 | PASSED |  |  | synced
2026-05-22 | OSD20 | DV116.19 | PQ3-Week3 | WT-26-0071 | TRUE | 10-3-143 | Building 10 | COATING SOLUTION PREP.-P | PW | 2026-05-23 | 2026-05-31 | 0 | 0 | 0 |  |  | 100 | PASSED |  |  | synced
2026-05-22 | OSD21 | SV116.12 | PQ3-Week3 | WT-26-0071 | TRUE | 10-3-144 | Building 10 | COATING-P | PW | 2026-05-23 | 2026-05-31 | 0 | 0 | 0 |  |  | 100 | PASSED |  |  | synced
2026-05-22 | OSD41 | DV116.02 | PQ3-Week3 | WT-26-0071 | TRUE | 10-1-115 | Building 10 | WASHING | PW | 2026-05-23 | 2026-05-31 | 0 | 0 | 0 |  |  | 100 | PASSED |  |  | synced
2026-05-22 | OSD42 | DV116.01 | PQ3-Week3 | WT-26-0071 | TRUE | 10-1-057 | Building 10 | WASHING-P | PW | 2026-05-23 | 2026-05-31 | 0 | 0 | 0 |  |  | 100 | PASSED |  |  | synced
2026-05-22 | BU19-14 | SV-14 | PQ3-Week3 | WT-26-0072 | TRUE | PROCESS WATER (B19) | Building 19 | AFTER RO SYSTEM NO.12 SV14 | PRW | 2026-05-23 | 2026-05-31 | 0 | 0 | 0 |  |  | 500 | PASSED |  |  | synced
2026-05-26 | GOLD05 | SV133.01 | PQ3-Week4 | WT-26-0073 | TRUE | WATER SYSTEM (B12) | Building 12 | After Storage tank (B12) | PW | 2026-05-26 | 2026-05-29 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-05-26 | GOLD06 | SV135.02 | PQ3-Week4 | WT-26-0073 | TRUE | WATER SYSTEM (B12) | Building 12 | After UV (B12) | PW | 2026-05-26 | 2026-05-29 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-05-26 | GOLD07 | SV137.01 | PQ3-Week4 | WT-26-0073 | TRUE | WATER SYSTEM (B12) | Building 12 | Return loop (B12) | PW | 2026-05-26 | 2026-05-29 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-05-26 | OLD06 | SV136.09 | PQ3-Week4 | WT-26-0073 | TRUE | 12-2-039 | Building 12 | MFG 1 | PW | 2026-05-26 | 2026-05-29 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-05-26 | OLD07 | SV136.10 | PQ3-Week4 | WT-26-0073 | TRUE | 12-2-041 | Building 12 | MFG 2 | PW | 2026-05-26 | 2026-05-29 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-05-26 | OLD08 | SV136.11 | PQ3-Week4 | WT-26-0073 | TRUE | 12-2-043 | Building 12 | MFG 3 | PW | 2026-05-26 | 2026-05-29 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-05-26 | OLD09 | SV136.13 | PQ3-Week4 | WT-26-0073 | TRUE | 12-2-043 | Building 12 | MFG 3 | PW | 2026-05-26 | 2026-05-29 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-05-26 | OLD11 | SV136.08 | PQ3-Week4 | WT-26-0073 | TRUE | 12-2-043 | Building 12 | MFG 3 | PW | 2026-05-26 | 2026-05-29 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-05-26 | OLD16 | SV136.14 | PQ3-Week4 | WT-26-0073 | TRUE | 12-2-045 | Building 12 | MFG 4 | PW | 2026-05-26 | 2026-05-29 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-05-26 | OLD18 | SV136.02 | PQ3-Week4 | WT-26-0073 | TRUE | 12-2-024 | Building 12 | LIQUORICE EXTRACT | PW | 2026-05-26 | 2026-05-29 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-05-26 | OLD32 | DV136.08 | PQ3-Week4 | WT-26-0073 | TRUE | 12-3-042 | Building 12 | SAMPLE PREPARATION | PW | 2026-05-26 | 2026-05-29 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-05-26 | OLD33 | DV136.09 | PQ3-Week4 | WT-26-0073 | TRUE | 12-3-042 | Building 12 | SAMPLE PREPARATION | PW | 2026-05-26 | 2026-05-29 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-05-26 | GOCL05 | SV123.01 | PQ3-Week4 | WT-26-0074 | TRUE | WATER SYSTEM (B16) | Building 16 | After Storage tank (B16) | PW | 2026-05-26 | 2026-05-29 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-05-26 | GOCL07 | SV125.02 | PQ3-Week4 | WT-26-0074 | TRUE | WATER SYSTEM (B16) | Building 16 | After UV (B16) | PW | 2026-05-26 | 2026-05-29 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-05-26 | GOCL08 | SV127.01 | PQ3-Week4 | WT-26-0074 | TRUE | WATER SYSTEM (B16) | Building 16 | Return loop (B16) | PW | 2026-05-26 | 2026-05-29 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-05-26 | OCL13 | SV126.19 | PQ3-Week4 | WT-26-0074 | TRUE | 16-3-087 | Building 16 | CIP 2 (EQUIPMENT REQUIREMENT) | PW | 2026-05-26 | 2026-05-29 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-05-26 | OCL14 | DV126.11 | PQ3-Week4 | WT-26-0074 | TRUE | 16-3-073 | Building 16 | MFG 4 (5000L) | PW | 2026-05-26 | 2026-05-29 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-05-26 | OCL15 | SV126.14 | PQ3-Week4 | WT-26-0074 | TRUE | 16-3-073 | Building 16 | MFG 4 (400L) | PW | 2026-05-26 | 2026-05-29 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-05-26 | OCL17 | SV126.15 | PQ3-Week4 | WT-26-0074 | TRUE | 16-3-075 | Building 16 | MFG 5 PROCESS (2000L) | PW | 2026-05-26 | 2026-05-29 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-05-26 | OCL21 | DV126.05 | PQ3-Week4 | WT-26-0074 | TRUE | 16-3-054 | Building 16 | WASHING | PW | 2026-05-26 | 2026-05-29 | 5 | 33 | 19 | COMMU: PW-M-2-26-005 |  | 100 | PASSED | FALSE |  | synced
2026-05-26 | OCL23 | SV126.04 | PQ3-Week4 | WT-26-0074 | TRUE | 16-2-010 | Building 16 | WATER SYSTEM (PSG) | PW | 2026-05-26 | 2026-05-29 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-05-29 | OCL13 | SV126.19 | PQ3-Week4 | WT-26-0080 | TRUE | 16-3-087 | Building 16 | CIP 2 (EQUIPMENT REQUIREMENT) | PW | 2026-05-30 | 2026-06-02 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-05-29 | GOSD08 | SV117.01 | PQ3-Week4 | WT-26-0075 | TRUE | WATER SYSTEM (B10) | Building 10 | Return loop (B10) | PW | 2026-05-30 | 2026-06-02 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-05-29 | OSD01 | SV116.15 | PQ3-Week4 | WT-26-0075 | TRUE | 10-4-012 | Building 10 | CIP SKID-1 FOR BIN WASHING-1 | PW | 2026-05-30 | 2026-06-02 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-05-29 | OSD02 | SV116.16 | PQ3-Week4 | WT-26-0075 | TRUE | 10-4-012 | Building 10 | WIP SKID-3 FOR GRANULATION POTENT | PW | 2026-05-30 | 2026-06-02 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-05-29 | OSD03 | SV116.17 | PQ3-Week4 | WT-26-0075 | TRUE | 10-4-012 | Building 10 | CIP SKID-2 FOR BIN WASHING-1 | PW | 2026-05-30 | 2026-06-02 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-05-29 | OSD04 | SV116.18 | PQ3-Week4 | WT-26-0075 | TRUE | 10-4-012 | Building 10 | WIP SKID-1 FOR GRANULATION NON POTENT | PW | 2026-05-30 | 2026-06-02 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-05-29 | OSD05 | SV116.19 | PQ3-Week4 | WT-26-0075 | TRUE | 10-4-012 | Building 10 | WIP SKID-2 FOR GRANULATION NON POTENT | PW | 2026-05-30 | 2026-06-02 | 8 | 19 | 14 | COMMU : PW-M-2-26-002 |  | 100 | PASSED | FALSE |  | synced
2026-05-29 | OSD34 | SV116.02 | PQ3-Week4 | WT-26-0075 | TRUE | 10-2-037 | Building 10 | SKID FOR BIN WASHING-2 | PW | 2026-05-30 | 2026-06-02 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-05-29 | OSD35 | SV116.01 | PQ3-Week4 | WT-26-0075 | TRUE | 10-2-021 | Building 10 | INSTRUMENT-1 | PW | 2026-05-30 | 2026-06-02 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-05-29 | OSD43 | DV116.26 | PQ3-Week4 | WT-26-0075 | TRUE | 10-4-015 | Building 10 | WATER SYSTEM ROOM | PW | 2026-05-30 | 2026-06-02 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-06-02 | GOCL01 | VB-05 (16) | PQ3-Week1 | WT-26-0076 | TRUE | WATER SYSTEM (B16) | Building 16 | After Chlorine circulation tank (B16) | PRW | 2026-06-03 | 2026-06-06 | 4 | 1 | 3 |  |  | 500 | PASSED | FALSE |  | synced
2026-06-02 | GOCL02 | V50-61 (16) | PQ3-Week1 | WT-26-0076 | TRUE | WATER SYSTEM (B16) | Building 16 | After Cartridge filter 5 µm (B16) | PRW | 2026-06-03 | 2026-06-06 | 1 | 0 | 1 |  |  | 500 | PASSED | FALSE |  | synced
2026-06-02 | GOCL03 | V50-11C (16) | PQ3-Week1 | WT-26-0076 | TRUE | WATER SYSTEM (B16) | Building 16 | After RO (Before EDI) (B16) | RO water | 2026-06-03 | 2026-06-06 | 0 | 0 | 0 |  |  | 500 | PASSED | FALSE |  | synced
2026-06-02 | GOCL04 | V50-39 (16) | PQ3-Week1 | WT-26-0076 | TRUE | WATER SYSTEM (B16) | Building 16 | After EDI (B16) | PW | 2026-06-03 | 2026-06-06 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-06-02 | GOCL08 | SV127.01 | PQ3-Week1 | WT-26-0076 | TRUE | WATER SYSTEM (B16) | Building 16 | Return loop (B16) | PW | 2026-06-03 | 2026-06-06 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-06-02 | OCL01 | DV126.02 | PQ3-Week1 | WT-26-0076 | TRUE | 16-1-082 | Building 16 | WASHING | PW | 2026-06-03 | 2026-06-06 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-06-02 | OCL02 | DV126.01 | PQ3-Week1 | WT-26-0076 | TRUE | 16-1-082 | Building 16 | WASHING | PW | 2026-06-03 | 2026-06-06 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-06-02 | OCL03 | SV126.02 | PQ3-Week1 | WT-26-0076 | TRUE | 16-1-098 | Building 16 | CIP/SIP (EQUIPMENT REQUIREMENT – 200L) | PW | 2026-06-03 | 2026-06-06 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-06-02 | OCL04 | DV126.03 | PQ3-Week1 | WT-26-0076 | TRUE | 16-1-098 | Building 16 | CIP/SIP (SINK WASHING) | PW | 2026-06-03 | 2026-06-06 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-06-02 | OCL05 | SV126.01 | PQ3-Week1 | WT-26-0076 | TRUE | 16-1-092 | Building 16 | LINEN WASHING | PW | 2026-06-03 | 2026-06-06 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-06-02 | OCL22 | SV126.03 | PQ3-Week1 | WT-26-0076 | TRUE | 16-2-010 | Building 16 | WATER SYSTEM (WFI) | PW | 2026-06-03 | 2026-06-06 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-06-02 | GOLD01 | VB-05 (12) | PQ3-Week1 | WT-26-0077 | TRUE | WATER SYSTEM (B12) | Building 12 | After Chlorine circulation tank | PRW | 2026-06-03 | 2026-06-06 |  |  |  |  | เก็บไม่ได้ | 500 | NOT-PASSED | FALSE |  | synced
2026-06-02 | GOLD02 | V50-61 (12) | PQ3-Week1 | WT-26-0077 | TRUE | WATER SYSTEM (B12) | Building 12 | After Cartridge filter 5 µm (B12) | PRW | 2026-06-03 | 2026-06-06 | 163 | 144 | 154 |  |  | 500 | PASSED | FALSE |  | synced
2026-06-02 | GOLD03 | V50-11C (12) | PQ3-Week1 | WT-26-0077 | TRUE | WATER SYSTEM (B12) | Building 12 | After RO (Before EDI) (B12) | RO water | 2026-06-03 | 2026-06-06 | 0 | 0 | 0 |  |  | 500 | PASSED | FALSE |  | synced
2026-06-02 | GOLD04 | V50-39 (12) | PQ3-Week1 | WT-26-0077 | TRUE | WATER SYSTEM (B12) | Building 12 | After EDI (B12) | PW | 2026-06-03 | 2026-06-06 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-06-02 | GOLD07 | SV137.01 | PQ3-Week1 | WT-26-0077 | TRUE | WATER SYSTEM (B12) | Building 12 | Return loop (B12) | PW | 2026-06-03 | 2026-06-06 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-06-02 | OLD21 | DV136.15 | PQ3-Week1 | WT-26-0077 | TRUE | 12-3-078 | Building 12 | GLASSWARE WASHING 2 | PW | 2026-06-03 | 2026-06-06 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-06-02 | OLD22 | DV136.13 | PQ3-Week1 | WT-26-0077 | TRUE | 12-3-057 | Building 12 | STERILIZATION | PW | 2026-06-03 | 2026-06-06 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-06-02 | OLD23 | SV136.18 | PQ3-Week1 | WT-26-0077 | TRUE | 12-3-059 | Building 12 | AUTOCLAVE | PW | 2026-06-03 | 2026-06-06 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-06-02 | OLD24 | DV136.11 | PQ3-Week1 | WT-26-0077 | TRUE | 12-3-059 | Building 12 | AUTOCLAVE | PW | 2026-06-03 | 2026-06-06 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-06-02 | OLD25 | DV136.12 | PQ3-Week1 | WT-26-0077 | TRUE | 12-3-056 | Building 12 | MEDIA PREPARATION | PW | 2026-06-03 | 2026-06-06 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-06-02 | OLD26 | DV136.10 | PQ3-Week1 | WT-26-0077 | TRUE | 12-3-056 | Building 12 | MEDIA PREPARATION | PW | 2026-06-03 | 2026-06-06 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-06-02 | OLD27 | DV136.14 | PQ3-Week1 | WT-26-0077 | TRUE | 12-3-074 | Building 12 | DECONTAMINATION | PW | 2026-06-03 | 2026-06-06 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-06-02 | OLD28 | DV136.18 | PQ3-Week1 | WT-26-0077 | TRUE | 12-3-037 | Building 12 | GLASSWARE WASHING 1 | PW | 2026-06-03 | 2026-06-06 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-06-02 | OLD29 | DV136.05 | PQ3-Week1 | WT-26-0077 | TRUE | 12-3-037 | Building 12 | GLASSWARE WASHING 1 | PW | 2026-06-03 | 2026-06-06 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-06-02 | OLD30 | DV136.06 | PQ3-Week1 | WT-26-0077 | TRUE | 12-3-037 | Building 12 | GLASSWARE WASHING 1 | PW | 2026-06-03 | 2026-06-06 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-06-05 | GOSD01 | VB-05(10) | PQ3-Week1 | WT-26-0078 | TRUE | WATER SYSTEM (B10) | Building 10 | After Chlorine circulation tank (B10) | PRW | 2026-06-05 | 2026-06-08 | 10 | 21 | 16 |  |  | 500 | PASSED | FALSE |  | synced
2026-06-05 | GOSD03 | V50-61(10) | PQ3-Week1 | WT-26-0078 | TRUE | WATER SYSTEM (B10) | Building 10 | After Cartridge filter 5 µm (B10) | PRW | 2026-06-05 | 2026-06-08 | 4 | 5 | 5 |  |  | 500 | PASSED | FALSE |  | synced
2026-06-05 | GOSD04 | V50-11C(10) | PQ3-Week1 | WT-26-0078 | TRUE | WATER SYSTEM (B10) | Building 10 | After RO (Before EDI) (B10) | RO water | 2026-06-05 | 2026-06-08 | 0 | 0 | 0 |  |  | 500 | PASSED | FALSE |  | synced
2026-06-05 | GOSD05 | V50-39(10) | PQ3-Week1 | WT-26-0078 | TRUE | WATER SYSTEM (B10) | Building 10 | After EDI (B10) | PW | 2026-06-05 | 2026-06-08 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-06-05 | GOSD08 | SV117.01 | PQ3-Week1 | WT-26-0078 | TRUE | WATER SYSTEM (B10) | Building 10 | Return loop (B10) | PW | 2026-06-05 | 2026-06-08 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-06-05 | OSD06 | DV116.18 | PQ3-Week1 | WT-26-0078 | TRUE | 10-3-111 | Building 10 | WET GRANULATION-5 | PW | 2026-06-05 | 2026-06-08 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-06-05 | OSD07 | DV116.16 | PQ3-Week1 | WT-26-0078 | TRUE | 10-3-107 | Building 10 | WET GRANULATION-2 | PW | 2026-06-05 | 2026-06-08 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-06-05 | OSD08 | SV116.11 | PQ3-Week1 | WT-26-0078 | TRUE | 10-3-107 | Building 10 | WET GRANULATION-2 | PW | 2026-06-05 | 2026-06-08 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-06-05 | OSD09 | DV116.14 | PQ3-Week1 | WT-26-0078 | TRUE | 10-3-086 | Building 10 | TOOL WASHING | PW | 2026-06-05 | 2026-06-08 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-06-05 | OSD10 | SV116.09 | PQ3-Week1 | WT-26-0078 | TRUE | 10-3-078 | Building 10 | WASHING | PW | 2026-06-05 | 2026-06-08 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-06-05 | OSD11 | DV116.13 | PQ3-Week1 | WT-26-0078 | TRUE | 10-3-078 | Building 10 | WASHING | PW | 2026-06-05 | 2026-06-08 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-06-05 | OSD12 | DV116.12 | PQ3-Week1 | WT-26-0078 | TRUE | 10-3-078 | Building 10 | WASHING | PW | 2026-06-05 | 2026-06-08 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-06-05 | OSD27 | DV116.17 | PQ3-Week1 | WT-26-0078 | TRUE | 10-3-117 | Building 10 | IPQC-2 | PW | 2026-06-05 | 2026-06-08 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-06-05 | OSD28 | DV116.15 | PQ3-Week1 | WT-26-0078 | TRUE | 10-3-104 | Building 10 | BINDER PREPARATION | PW | 2026-06-05 | 2026-06-08 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-06-05 | BU19-14 | SV-14 | PQ3-Week1 | WT-26-0079 | TRUE | PROCESS WATER (B19) | Building 19 | AFTER RO SYSTEM NO.12 SV14 | PRW | 2026-06-05 | 2026-06-08 | 130 | 138 | 134 |  |  | 500 | PASSED | FALSE |  | synced
2026-06-09 | GOCL05 | SV123.01 | PQ3-Week2 | WT-26-0081 | TRUE | WATER SYSTEM (B16) | Building 16 | After Storage tank (B16) | PW | 2026-06-10 | 2026-06-13 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-06-09 | GOCL07 | SV125.02 | PQ3-Week2 | WT-26-0081 | TRUE | WATER SYSTEM (B16) | Building 16 | After UV (B16) | PW | 2026-06-10 | 2026-06-13 | 1 | 0 | 1 |  |  | 100 | PASSED | FALSE |  | synced
2026-06-09 | GOCL08 | SV127.01 | PQ3-Week2 | WT-26-0081 | TRUE | WATER SYSTEM (B16) | Building 16 | Return loop (B16) | PW | 2026-06-10 | 2026-06-13 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-06-09 | OCL09 | DV126.10 | PQ3-Week2 | WT-26-0081 | TRUE | 16-3-069 | Building 16 | MFG 2 | PW | 2026-06-10 | 2026-06-13 | 9 | 1 | 5 |  |  | 100 | PASSED | FALSE |  | synced
2026-06-09 | OCL10 | DV126.06 | PQ3-Week2 | WT-26-0081 | TRUE | 16-3-069 | Building 16 | MFG 2 | PW | 2026-06-10 | 2026-06-13 | 23 | 22 | 23 | COMMU: PW-M-2-26-003 |  | 100 | PASSED | FALSE |  | synced
2026-06-09 | OCL11 | SV126.10 | PQ3-Week2 | WT-26-0081 | TRUE | 16-3-071 | Building 16 | MFG 3 (1200L) | PW | 2026-06-10 | 2026-06-13 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-06-09 | OCL12 | SV126.09 | PQ3-Week2 | WT-26-0081 | TRUE | 16-3-071 | Building 16 | MFG 3 (5000L) | PW | 2026-06-10 | 2026-06-13 | 1 | 0 | 1 |  |  | 100 | PASSED | FALSE |  | synced
2026-06-09 | OCL19 | DV126.07 | PQ3-Week2 | WT-26-0081 | TRUE | 16-3-077 | Building 16 | MFG 6 | PW | 2026-06-10 | 2026-06-13 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-06-09 | OCL18 | DV126.08 | PQ3-Week2 | WT-26-0081 | TRUE | 16-3-077 | Building 16 | MFG 6 | PW | 2026-06-10 | 2026-06-13 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-06-09 | GOLD05 | SV133.01 | PQ3-Week2 | WT-26-0082 | TRUE | WATER SYSTEM (B12) | Building 12 | After Storage tank (B12) | PW | 2026-06-10 | 2026-06-13 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-06-09 | GOLD06 | SV135.02 | PQ3-Week2 | WT-26-0082 | TRUE | WATER SYSTEM (B12) | Building 12 | After UV (B12) | PW | 2026-06-10 | 2026-06-13 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-06-09 | GOLD07 | SV137.01 | PQ3-Week2 | WT-26-0082 | TRUE | WATER SYSTEM (B12) | Building 12 | Return loop (B12) | PW | 2026-06-10 | 2026-06-13 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-06-09 | OLD03 | SV136.12 | PQ3-Week2 | WT-26-0082 | TRUE | 12-2-036 | Building 12 | CIP 1 | PW | 2026-06-10 | 2026-06-13 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-06-09 | OLD04 | SV136.07 | PQ3-Week2 | WT-26-0082 | TRUE | 12-2-034 | Building 12 | SYRUP PREPARATION | PW | 2026-06-10 | 2026-06-13 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-06-09 | OLD05 | SV136.06 | PQ3-Week2 | WT-26-0082 | TRUE | 12-2-034 | Building 12 | SYRUP PREPARATION | PW | 2026-06-10 | 2026-06-13 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-06-09 | OLD12 | SV136.03 | PQ3-Week2 | WT-26-0082 | TRUE | 12-2-032 | Building 12 | CAMPHORATED OPIUM TINCTURE | PW | 2026-06-10 | 2026-06-13 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-06-09 | OLD13 | SV136.05 | PQ3-Week2 | WT-26-0082 | TRUE | 12-2-032 | Building 12 | CAMPHORATED OPIUM TINCTURE | PW | 2026-06-10 | 2026-06-13 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-06-09 | OLD14 | SV136.04 | PQ3-Week2 | WT-26-0082 | TRUE | 12-2-030 | Building 12 | OPIUM TINCTURE | PW | 2026-06-10 | 2026-06-13 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-06-09 | OLD15 | DV136.02 | PQ3-Week2 | WT-26-0082 | TRUE | 12-2-028 | Building 12 | ALCOHOL STORAGE | PW | 2026-06-10 | 2026-06-13 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-06-09 | OLD31 | DV136.07 | PQ3-Week2 | WT-26-0082 | TRUE | 12-3-039 | Building 12 | INSTRUMENT 7 | PW | 2026-06-10 | 2026-06-13 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-06-12 |  | B11 | PQ3-Week2 |  | FALSE | #N/A |  | #N/A | #N/A | 2026-06-12 | 2026-06-15 | 0 | 0 | 0 |  |  | #N/A | NA | FALSE
2026-06-12 | GOSD06 | SV113.01 | PQ3-Week2 | WT-26-0083 | TRUE | WATER SYSTEM (B10) | Building 10 | After Storage tank (B10) | PW | 2026-06-12 | 2026-06-15 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-06-12 | GOSD07 | SV115.02 | PQ3-Week2 | WT-26-0083 | TRUE | WATER SYSTEM (B10) | Building 10 | After UV (B10) | PW | 2026-06-12 | 2026-06-15 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-06-12 | GOSD08 | SV117.01 | PQ3-Week2 | WT-26-0083 | TRUE | WATER SYSTEM (B10) | Building 10 | Return loop (B10) | PW | 2026-06-12 | 2026-06-15 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-06-12 | OSD22 | SV116.05 | PQ3-Week2 | WT-26-0083 | TRUE | 10-3-062 | Building 10 | COATING ROOM-3 | PW | 2026-06-12 | 2026-06-15 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-06-12 | OSD23 | SV116.04 | PQ3-Week2 | WT-26-0083 | TRUE | 10-3-061 | Building 10 | COATING ROOM-2 | PW | 2026-06-12 | 2026-06-15 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-06-12 | OSD24 | DV116.09 | PQ3-Week2 | WT-26-0083 | TRUE | 10-3-060 | Building 10 | COATING SOLUTION PREP.-2 | PW | 2026-06-12 | 2026-06-15 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-06-12 | OSD25 | DV116.08 | PQ3-Week2 | WT-26-0083 | TRUE | 10-3-059 | Building 10 | COATING SOLUTION PREP.-1 | PW | 2026-06-12 | 2026-06-15 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-06-12 | OSD26 | SV116.03 | PQ3-Week2 | WT-26-0083 | TRUE | 10-3-058 | Building 10 | COATING ROOM-1 | PW | 2026-06-12 | 2026-06-15 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-06-12 | OSD29 | SV116.08 | PQ3-Week2 | WT-26-0083 | TRUE | 10-3-067 | Building 10 | COATING ROOM-6 | PW | 2026-06-12 | 2026-06-15 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-06-12 | OSD30 | DV116.11 | PQ3-Week2 | WT-26-0083 | TRUE | 10-3-066 | Building 10 | COATING SOLUTION PREP.-4 | PW | 2026-06-12 | 2026-06-15 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-06-12 | OSD31 | DV116.10 | PQ3-Week2 | WT-26-0083 | TRUE | 10-3-065 | Building 10 | COATING SOLUTION PREP.-3 | PW | 2026-06-12 | 2026-06-15 | 23 | 28 | 26 | COMMU: PW-M-2-26-004 |  | 100 | PASSED | FALSE |  | synced
2026-06-12 | OSD32 | SV116.07 | PQ3-Week2 | WT-26-0083 | TRUE | 10-3-064 | Building 10 | COATING ROOM-5 | PW | 2026-06-12 | 2026-06-15 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-06-12 | OSD33 | SV116.06 | PQ3-Week2 | WT-26-0083 | TRUE | 10-3-063 | Building 10 | COATING ROOM-4 | PW | 2026-06-12 | 2026-06-15 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-06-12 | OSD36 | DV116.03 | PQ3-Week2 | WT-26-0083 | TRUE | 10-2-034 | Building 10 | SAMPLE PREPARATION | PW | 2026-06-12 | 2026-06-15 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-06-12 | OSD37 | DV116.06 | PQ3-Week2 | WT-26-0083 | TRUE | 10-2-034 | Building 10 | SAMPLE PREPARATION | PW | 2026-06-12 | 2026-06-15 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-06-12 | OSD38 | DV116.07 | PQ3-Week2 | WT-26-0083 | TRUE | 10-2-032 | Building 10 | GLASS-WARE WASHING | PW | 2026-06-12 | 2026-06-15 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-06-12 | OSD39 | DV116.05 | PQ3-Week2 | WT-26-0083 | TRUE | 10-2-032 | Building 10 | GLASS-WARE WASHING | PW | 2026-06-12 | 2026-06-15 | 1 | 0 | 1 |  |  | 100 | PASSED | FALSE |  | synced
2026-06-12 | OSD40 | DV116.04 | PQ3-Week2 | WT-26-0083 | TRUE | 10-2-037 | Building 10 | SKID FOR BIN WASHING-1 | PW | 2026-06-12 | 2026-06-15 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-06-16 | GOLD01 | VB-05 (12) | PQ3-Week3 | WT-26-0084 | TRUE | WATER SYSTEM (B12) | Building 12 | After Chlorine circulation tank | PRW | 2026-06-17 | 2026-06-20 | 0 | 0 | 0 |  |  | 500 | PASSED | FALSE |  | synced
2026-06-16 | GOLD02 | V50-61 (12) | PQ3-Week3 | WT-26-0084 | TRUE | WATER SYSTEM (B12) | Building 12 | After Cartridge filter 5 µm (B12) | PRW | 2026-06-17 | 2026-06-20 | 188 | 165 | 177 |  |  | 500 | PASSED | FALSE |  | synced
2026-06-16 | GOLD03 | V50-11C (12) | PQ3-Week3 | WT-26-0084 | TRUE | WATER SYSTEM (B12) | Building 12 | After RO (Before EDI) (B12) | RO water | 2026-06-17 | 2026-06-20 | 0 | 0 | 0 |  |  | 500 | PASSED | FALSE |  | synced
2026-06-16 | GOLD04 | V50-39 (12) | PQ3-Week3 | WT-26-0084 | TRUE | WATER SYSTEM (B12) | Building 12 | After EDI (B12) | PW | 2026-06-17 | 2026-06-20 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-06-16 | GOLD07 | SV137.01 | PQ3-Week3 | WT-26-0084 | TRUE | WATER SYSTEM (B12) | Building 12 | Return loop (B12) | PW | 2026-06-17 | 2026-06-20 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-06-16 | OLD01 | DV136.17 | PQ3-Week3 | WT-26-0084 | TRUE | 12-2-065 | Building 12 | WASHING | PW | 2026-06-17 | 2026-06-20 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-06-16 | OLD02 | SV136.16 | PQ3-Week3 | WT-26-0084 | TRUE | 12-2-057 | Building 12 | CIP 2 | PW | 2026-06-17 | 2026-06-20 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-06-16 | OLD10 | SV136.15 | PQ3-Week3 | WT-26-0084 | TRUE | 12-2-055 | Building 12 | CIP 3 | PW | 2026-06-17 | 2026-06-20 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-06-16 | OLD17 | DV136.03 | PQ3-Week3 | WT-26-0084 | TRUE | 12-2-053 | Building 12 | IPQC | PW | 2026-06-17 | 2026-06-20 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-06-16 | OLD19 | DV136.01 | PQ3-Week3 | WT-26-0084 | TRUE | 12-1-035 | Building 12 | SUGAR TRANSFERRING | PW | 2026-06-17 | 2026-06-20 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-06-16 | OLD20 | DV136.16 | PQ3-Week3 | WT-26-0084 | TRUE | 12-1-064 | Building 12 | WASHING | PW | 2026-06-17 | 2026-06-20 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-06-16 | OLD34 | DV136.04 | PQ3-Week3 | WT-26-0084 | TRUE | 12-2-077 | Building 12 | WATER SYSTEM ROOM | PW | 2026-06-17 | 2026-06-20 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-06-16 | GOCL01 | VB-05 (16) | PQ3-Week3 | WT-26-0085 | TRUE | WATER SYSTEM (B16) | Building 16 | After Chlorine circulation tank (B16) | PRW | 2026-06-17 | 2026-06-20 | 0 | 0 | 0 |  |  | 500 | PASSED | FALSE |  | synced
2026-06-16 | GOCL02 | V50-61 (16) | PQ3-Week3 | WT-26-0085 | TRUE | WATER SYSTEM (B16) | Building 16 | After Cartridge filter 5 µm (B16) | PRW | 2026-06-17 | 2026-06-20 | 0 | 0 | 0 |  |  | 500 | PASSED | FALSE |  | synced
2026-06-16 | GOCL03 | V50-11C (16) | PQ3-Week3 | WT-26-0085 | TRUE | WATER SYSTEM (B16) | Building 16 | After RO (Before EDI) (B16) | RO water | 2026-06-17 | 2026-06-20 | 0 | 0 | 0 |  |  | 500 | PASSED | FALSE |  | synced
2026-06-16 | GOCL04 | V50-39 (16) | PQ3-Week3 | WT-26-0085 | TRUE | WATER SYSTEM (B16) | Building 16 | After EDI (B16) | PW | 2026-06-17 | 2026-06-20 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-06-16 | GOCL08 | SV127.01 | PQ3-Week3 | WT-26-0085 | TRUE | WATER SYSTEM (B16) | Building 16 | Return loop (B16) | PW | 2026-06-17 | 2026-06-20 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-06-16 | OCL06 | SV126.06 | PQ3-Week3 | WT-26-0085 | TRUE | 16-3-067 | Building 16 | MFG 1 | PW | 2026-06-17 | 2026-06-20 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-06-16 | OCL07 | SV126.21 | PQ3-Week3 | WT-26-0085 | TRUE | 16-3-090 | Building 16 | CIP 1 (EQUIPMENT REQUIREMENT) | PW | 2026-06-17 | 2026-06-20 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-06-16 | OCL08 | DV126.09 | PQ3-Week3 | WT-26-0085 | TRUE | 16-3-090 | Building 16 | CIP 1 (ZINK WASHING) | PW | 2026-06-17 | 2026-06-20 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-06-16 | OCL16 | SV126.18 | PQ3-Week3 | WT-26-0085 | TRUE | 16-3-085 | Building 16 | CIP 3 (EQUIPMENT REQUIREMENT) | PW | 2026-06-17 | 2026-06-20 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-06-16 | OCL20 | SV126.05 | PQ3-Week3 | WT-26-0085 | TRUE | 16-3-049 | Building 16 | LINEN WASHING | PW | 2026-06-17 | 2026-06-20 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-06-16 | OCL24 | DV126.04 | PQ3-Week3 | WT-26-0085 | TRUE | 16-2-010 | Building 16 | WATER SYSTEM (PW) | PW | 2026-06-17 | 2026-06-20 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-06-19 | GOSD01 | VB-05(10) | PQ3-Week3 | WT-26-0086 | TRUE | WATER SYSTEM (B10) | Building 10 | After Chlorine circulation tank (B10) | PRW | 2026-06-19 | 2026-06-22 | 120 | 47 | 84 |  |  | 500 | PASSED | FALSE |  | synced
2026-06-19 | GOSD03 | V50-61(10) | PQ3-Week3 | WT-26-0086 | TRUE | WATER SYSTEM (B10) | Building 10 | After Cartridge filter 5 µm (B10) | PRW | 2026-06-19 | 2026-06-22 | 52 | 38 | 45 |  |  | 500 | PASSED | FALSE |  | synced
2026-06-19 | GOSD04 | V50-11C(10) | PQ3-Week3 | WT-26-0086 | TRUE | WATER SYSTEM (B10) | Building 10 | After RO (Before EDI) (B10) | RO water | 2026-06-19 | 2026-06-22 | 0 | 0 | 0 |  |  | 500 | PASSED | FALSE |  | synced
2026-06-19 | GOSD05 | V50-39(10) | PQ3-Week3 | WT-26-0086 | TRUE | WATER SYSTEM (B10) | Building 10 | After EDI (B10) | PW | 2026-06-19 | 2026-06-22 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-06-19 | GOSD08 | SV117.01 | PQ3-Week3 | WT-26-0086 | TRUE | WATER SYSTEM (B10) | Building 10 | Return loop (B10) | PW | 2026-06-19 | 2026-06-22 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-06-19 | OSD13 | DV116.25 | PQ3-Week3 | WT-26-0086 | TRUE | 10-3-171 | Building 10 | TOOL WASHING-P | PW | 2026-06-19 | 2026-06-22 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-06-19 | OSD14 | DV116.24 | PQ3-Week3 | WT-26-0086 | TRUE | 10-3-163 | Building 10 | WET GRANULATION 1-P | PW | 2026-06-19 | 2026-06-22 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-06-19 | OSD15 | DV116.23 | PQ3-Week3 | WT-26-0086 | TRUE | 10-3-159 | Building 10 | BINDER PREPARATION-P | PW | 2026-06-19 | 2026-06-22 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-06-19 | OSD16 | DV116.21 | PQ3-Week3 | WT-26-0086 | TRUE | 10-3-152 | Building 10 | WASHING-P | PW | 2026-06-19 | 2026-06-22 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-06-19 | OSD17 | DV116.22 | PQ3-Week3 | WT-26-0086 | TRUE | 10-3-152 | Building 10 | WASHING-P | PW | 2026-06-19 | 2026-06-22 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-06-19 | OSD18 | SV116.13 | PQ3-Week3 | WT-26-0086 | TRUE | 10-3-152 | Building 10 | WASHING-P | PW | 2026-06-19 | 2026-06-22 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-06-19 | OSD19 | DV116.20 | PQ3-Week3 | WT-26-0086 | TRUE | 10-3-149 | Building 10 | IPQC-1-P | PW | 2026-06-19 | 2026-06-22 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-06-19 | OSD20 | DV116.19 | PQ3-Week3 | WT-26-0086 | TRUE | 10-3-143 | Building 10 | COATING SOLUTION PREP.-P | PW | 2026-06-19 | 2026-06-22 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-06-19 | OSD21 | SV116.12 | PQ3-Week3 | WT-26-0086 | TRUE | 10-3-144 | Building 10 | COATING-P | PW | 2026-06-19 | 2026-06-22 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-06-19 | OSD41 | DV116.02 | PQ3-Week3 | WT-26-0086 | TRUE | 10-1-115 | Building 10 | WASHING | PW | 2026-06-19 | 2026-06-22 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-06-19 | OSD42 | DV116.01 | PQ3-Week3 | WT-26-0086 | TRUE | 10-1-057 | Building 10 | WASHING-P | PW | 2026-06-19 | 2026-06-22 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-06-19 | BU19-14 | SV-14 | PQ3-Week3 | WT-26-0087 | TRUE | PROCESS WATER (B19) | Building 19 | AFTER RO SYSTEM NO.12 SV14 | PRW | 2026-06-19 | 2026-06-22 | 5 | 4 | 5 |  |  | 500 | PASSED | FALSE |  | synced
2026-06-17 | OCL13 | SV126.19 | PQ3-Week3 | WT-26-0088 | TRUE | 16-3-087 | Building 16 | CIP 2 (EQUIPMENT REQUIREMENT) | PW | 2026-06-18 | 2026-06-21 | 4 | 5 | 5 |  |  | 100 | PASSED | FALSE |  | synced
2026-06-17 | OCL15 | SV126.14 | PQ3-Week3 | WT-26-0088 | TRUE | 16-3-073 | Building 16 | MFG 4 (400L) | PW | 2026-06-18 | 2026-06-21 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-06-23 | GOCL05 | SV123.01 | PQ3-Week4 | WT-26-0089 | TRUE | WATER SYSTEM (B16) | Building 16 | After Storage tank (B16) | PW | 2026-06-24 | 2026-06-27 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-06-23 | GOCL07 | SV125.02 | PQ3-Week4 | WT-26-0089 | TRUE | WATER SYSTEM (B16) | Building 16 | After UV (B16) | PW | 2026-06-24 | 2026-06-27 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-06-23 | GOCL08 | SV127.01 | PQ3-Week4 | WT-26-0089 | TRUE | WATER SYSTEM (B16) | Building 16 | Return loop (B16) | PW | 2026-06-24 | 2026-06-27 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-06-23 | OCL14 | DV126.11 | PQ3-Week4 | WT-26-0089 | TRUE | 16-3-073 | Building 16 | MFG 4 (5000L) | PW | 2026-06-24 | 2026-06-27 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-06-23 | OCL17 | SV126.15 | PQ3-Week4 | WT-26-0089 | TRUE | 16-3-075 | Building 16 | MFG 5 PROCESS (2000L) | PW | 2026-06-24 | 2026-06-27 | 1 | 0 | 1 |  |  | 100 | PASSED | FALSE |  | synced
2026-06-23 | OCL21 | DV126.05 | PQ3-Week4 | WT-26-0089 | TRUE | 16-3-054 | Building 16 | WASHING | PW | 2026-06-24 | 2026-06-27 | 33 | 37 | 35 | COMMU : PW-M-2-26-007 |  | 100 | PASSED | FALSE |  | synced
2026-06-23 | OCL23 | SV126.04 | PQ3-Week4 | WT-26-0089 | TRUE | 16-2-010 | Building 16 | WATER SYSTEM (PSG) | PW | 2026-06-24 | 2026-06-27 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-06-23 | GOLD05 | SV133.01 | PQ3-Week4 | WT-26-0090 | TRUE | WATER SYSTEM (B12) | Building 12 | After Storage tank (B12) | PW | 2026-06-24 | 2026-06-27 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-06-23 | GOLD06 | SV135.02 | PQ3-Week4 | WT-26-0090 | TRUE | WATER SYSTEM (B12) | Building 12 | After UV (B12) | PW | 2026-06-24 | 2026-06-27 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-06-23 | GOLD07 | SV137.01 | PQ3-Week4 | WT-26-0090 | TRUE | WATER SYSTEM (B12) | Building 12 | Return loop (B12) | PW | 2026-06-24 | 2026-06-27 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-06-23 | OLD06 | SV136.09 | PQ3-Week4 | WT-26-0090 | TRUE | 12-2-039 | Building 12 | MFG 1 | PW | 2026-06-24 | 2026-06-27 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-06-23 | OLD07 | SV136.10 | PQ3-Week4 | WT-26-0090 | TRUE | 12-2-041 | Building 12 | MFG 2 | PW | 2026-06-24 | 2026-06-27 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-06-23 | OLD08 | SV136.11 | PQ3-Week4 | WT-26-0090 | TRUE | 12-2-043 | Building 12 | MFG 3 | PW | 2026-06-24 | 2026-06-27 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-06-23 | OLD09 | SV136.13 | PQ3-Week4 | WT-26-0090 | TRUE | 12-2-043 | Building 12 | MFG 3 | PW | 2026-06-24 | 2026-06-27 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-06-23 | OLD11 | SV136.08 | PQ3-Week4 | WT-26-0090 | TRUE | 12-2-043 | Building 12 | MFG 3 | PW | 2026-06-24 | 2026-06-27 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-06-23 | OLD16 | SV136.14 | PQ3-Week4 | WT-26-0090 | TRUE | 12-2-045 | Building 12 | MFG 4 | PW | 2026-06-24 | 2026-06-27 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-06-23 | OLD18 | SV136.02 | PQ3-Week4 | WT-26-0090 | TRUE | 12-2-024 | Building 12 | LIQUORICE EXTRACT | PW | 2026-06-24 | 2026-06-27 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-06-23 | OLD32 | DV136.08 | PQ3-Week4 | WT-26-0090 | TRUE | 12-3-042 | Building 12 | SAMPLE PREPARATION | PW | 2026-06-24 | 2026-06-27 | 2 | 5 | 4 |  |  | 100 | PASSED | FALSE |  | synced
2026-06-23 | OLD33 | DV136.09 | PQ3-Week4 | WT-26-0090 | TRUE | 12-3-042 | Building 12 | SAMPLE PREPARATION | PW | 2026-06-24 | 2026-06-27 | 37 | 6 | 22 | COMMU : PW-M-2-26-006 |  | 100 | PASSED | FALSE |  | synced
2026-06-26 | GOSD06 | SV113.01 | PQ3-Week4 | WT-26-0091 | TRUE | WATER SYSTEM (B10) | Building 10 | After Storage tank (B10) | PW | 2026-06-26 | 2026-06-06 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-06-26 | GOSD07 | SV115.02 | PQ3-Week4 | WT-26-0091 | TRUE | WATER SYSTEM (B10) | Building 10 | After UV (B10) | PW | 2026-06-26 | 2026-06-29 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-06-26 | GOSD08 | SV117.01 | PQ3-Week4 | WT-26-0091 | TRUE | WATER SYSTEM (B10) | Building 10 | Return loop (B10) | PW | 2026-06-26 | 2026-06-29 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-06-26 | OSD01 | SV116.15 | PQ3-Week4 | WT-26-0091 | TRUE | 10-4-012 | Building 10 | CIP SKID-1 FOR BIN WASHING-1 | PW | 2026-06-26 | 2026-06-29 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-06-26 | OSD02 | SV116.16 | PQ3-Week4 | WT-26-0091 | TRUE | 10-4-012 | Building 10 | WIP SKID-3 FOR GRANULATION POTENT | PW | 2026-06-26 | 2026-06-29 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-06-26 | OSD03 | SV116.17 | PQ3-Week4 | WT-26-0091 | TRUE | 10-4-012 | Building 10 | CIP SKID-2 FOR BIN WASHING-1 | PW | 2026-06-26 | 2026-06-29 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-06-26 | OSD04 | SV116.18 | PQ3-Week4 | WT-26-0091 | TRUE | 10-4-012 | Building 10 | WIP SKID-1 FOR GRANULATION NON POTENT | PW | 2026-06-26 | 2026-06-29 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-06-26 | OSD05 | SV116.19 | PQ3-Week4 | WT-26-0091 | TRUE | 10-4-012 | Building 10 | WIP SKID-2 FOR GRANULATION NON POTENT | PW | 2026-06-26 | 2026-06-29 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-06-26 | OSD34 | SV116.02 | PQ3-Week4 | WT-26-0091 | TRUE | 10-2-037 | Building 10 | SKID FOR BIN WASHING-2 | PW | 2026-06-26 | 2026-06-29 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-06-26 | OSD35 | SV116.01 | PQ3-Week4 | WT-26-0091 | TRUE | 10-2-021 | Building 10 | INSTRUMENT-1 | PW | 2026-06-26 | 2026-06-29 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-06-26 | OSD43 | DV116.26 | PQ3-Week4 | WT-26-0091 | TRUE | 10-4-015 | Building 10 | WATER SYSTEM ROOM | PW | 2026-06-26 | 2026-06-29 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-07-01 | GOLD01 | VB-05 (12) | PQ3-Week1 | WT-26-0092 | TRUE | WATER SYSTEM (B12) | Building 12 | After Chlorine circulation tank | PRW | 2026-07-01 | 2026-07-06 | 675 | 500 | 588 | COMMU : TS-M-2-26-001 |  | 500 | NOT-PASSED | FALSE |  | synced
2026-07-01 | GOLD02 | V50-61 (12) | PQ3-Week1 | WT-26-0092 | TRUE | WATER SYSTEM (B12) | Building 12 | After Cartridge filter 5 µm (B12) | PRW | 2026-07-01 | 2026-07-06 | 215 | 408 | 312 |  |  | 500 | PASSED | FALSE |  | synced
2026-07-01 | GOLD03 | V50-11C (12) | PQ3-Week1 | WT-26-0092 | TRUE | WATER SYSTEM (B12) | Building 12 | After RO (Before EDI) (B12) | RO water | 2026-07-01 | 2026-07-06 | 0 | 0 | 0 |  |  | 500 | PASSED | FALSE |  | synced
2026-07-01 | GOLD04 | V50-39 (12) | PQ3-Week1 | WT-26-0092 | TRUE | WATER SYSTEM (B12) | Building 12 | After EDI (B12) | PW | 2026-07-01 | 2026-07-06 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-07-01 | GOLD07 | SV137.01 | PQ3-Week1 | WT-26-0092 | TRUE | WATER SYSTEM (B12) | Building 12 | Return loop (B12) | PW | 2026-07-01 | 2026-07-06 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-07-01 | OLD21 | DV136.15 | PQ3-Week1 | WT-26-0092 | TRUE | 12-3-078 | Building 12 | GLASSWARE WASHING 2 | PW | 2026-07-01 | 2026-07-06 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-07-01 | OLD22 | DV136.13 | PQ3-Week1 | WT-26-0092 | TRUE | 12-3-057 | Building 12 | STERILIZATION | PW | 2026-07-01 | 2026-07-06 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-07-01 | OLD23 | SV136.18 | PQ3-Week1 | WT-26-0092 | TRUE | 12-3-059 | Building 12 | AUTOCLAVE | PW | 2026-07-01 | 2026-07-06 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-07-01 | OLD24 | DV136.11 | PQ3-Week1 | WT-26-0092 | TRUE | 12-3-059 | Building 12 | AUTOCLAVE | PW | 2026-07-01 | 2026-07-06 | 8 | 13 | 11 | COMMU : PW-M-2-26-008 |  | 100 | PASSED | FALSE |  | synced
2026-07-01 | OLD25 | DV136.12 | PQ3-Week1 | WT-26-0092 | TRUE | 12-3-056 | Building 12 | MEDIA PREPARATION | PW | 2026-07-01 | 2026-07-06 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-07-01 | OLD26 | DV136.10 | PQ3-Week1 | WT-26-0092 | TRUE | 12-3-056 | Building 12 | MEDIA PREPARATION | PW | 2026-07-01 | 2026-07-06 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-07-01 | OLD27 | DV136.14 | PQ3-Week1 | WT-26-0092 | TRUE | 12-3-074 | Building 12 | DECONTAMINATION | PW | 2026-07-01 | 2026-07-06 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-07-01 | OLD28 | DV136.18 | PQ3-Week1 | WT-26-0092 | TRUE | 12-3-037 | Building 12 | GLASSWARE WASHING 1 | PW | 2026-07-01 | 2026-07-06 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-07-01 | OLD29 | DV136.05 | PQ3-Week1 | WT-26-0092 | TRUE | 12-3-037 | Building 12 | GLASSWARE WASHING 1 | PW | 2026-07-01 | 2026-07-06 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-07-01 | OLD30 | DV136.06 | PQ3-Week1 | WT-26-0092 | TRUE | 12-3-037 | Building 12 | GLASSWARE WASHING 1 | PW | 2026-07-01 | 2026-07-06 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-07-01 | GOCL01 | VB-05 (16) | PQ3-Week1 | WT-26-0093 | TRUE | WATER SYSTEM (B16) | Building 16 | After Chlorine circulation tank (B16) | PRW | 2026-07-01 | 2026-07-06 | 707 | 701 | 704 | COMMU: TS-M-2-26-002 |  | 500 | NOT-PASSED | FALSE |  | synced
2026-07-01 | GOCL02 | V50-61 (16) | PQ3-Week1 | WT-26-0093 | TRUE | WATER SYSTEM (B16) | Building 16 | After Cartridge filter 5 µm (B16) | PRW | 2026-07-01 | 2026-07-06 | 223 | 173 | 198 |  |  | 500 | PASSED | FALSE |  | synced
2026-07-01 | GOCL03 | V50-11C (16) | PQ3-Week1 | WT-26-0093 | TRUE | WATER SYSTEM (B16) | Building 16 | After RO (Before EDI) (B16) | RO water | 2026-07-01 | 2026-07-06 | 0 | 0 | 0 |  |  | 500 | PASSED | FALSE |  | synced
2026-07-01 | GOCL04 | V50-39 (16) | PQ3-Week1 | WT-26-0093 | TRUE | WATER SYSTEM (B16) | Building 16 | After EDI (B16) | PW | 2026-07-01 | 2026-07-06 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-07-01 | GOCL08 | SV127.01 | PQ3-Week1 | WT-26-0093 | TRUE | WATER SYSTEM (B16) | Building 16 | Return loop (B16) | PW | 2026-07-01 | 2026-07-06 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-07-01 | OCL01 | DV126.02 | PQ3-Week1 | WT-26-0093 | TRUE | 16-1-082 | Building 16 | WASHING | PW | 2026-07-01 | 2026-07-06 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-07-01 | OCL02 | DV126.01 | PQ3-Week1 | WT-26-0093 | TRUE | 16-1-082 | Building 16 | WASHING | PW | 2026-07-01 | 2026-07-06 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-07-01 | OCL03 | SV126.02 | PQ3-Week1 | WT-26-0093 | TRUE | 16-1-098 | Building 16 | CIP/SIP (EQUIPMENT REQUIREMENT – 200L) | PW | 2026-07-01 | 2026-07-06 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-07-01 | OCL04 | DV126.03 | PQ3-Week1 | WT-26-0093 | TRUE | 16-1-098 | Building 16 | CIP/SIP (SINK WASHING) | PW | 2026-07-01 | 2026-07-06 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-07-01 | OCL05 | SV126.01 | PQ3-Week1 | WT-26-0093 | TRUE | 16-1-092 | Building 16 | LINEN WASHING | PW | 2026-07-01 | 2026-07-06 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-07-01 | OCL22 | SV126.03 | PQ3-Week1 | WT-26-0093 | TRUE | 16-2-010 | Building 16 | WATER SYSTEM (WFI) | PW | 2026-07-01 | 2026-07-06 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-07-03 | BU19-14 | SV-14 | PQ3-Week1 | WT-26-0094 | TRUE | PROCESS WATER (B19) | Building 19 | AFTER RO SYSTEM NO.12 SV14 | PRW | 2026-07-03 | 2026-07-06 | 390 | 308 | 349 |  |  | 500 | PASSED | FALSE |  | synced
2026-07-03 | GOSD01 | VB-05(10) | PQ3-Week1 | WT-26-0095 | TRUE | WATER SYSTEM (B10) | Building 10 | After Chlorine circulation tank (B10) | PRW | 2026-07-03 | 2026-07-06 | 246 | 65 | 156 |  |  | 500 | PASSED | FALSE |  | synced
2026-07-03 | GOSD03 | V50-61(10) | PQ3-Week1 | WT-26-0095 | TRUE | WATER SYSTEM (B10) | Building 10 | After Cartridge filter 5 µm (B10) | PRW | 2026-07-03 | 2026-07-06 | 38 | 74 | 56 |  |  | 500 | PASSED | FALSE |  | synced
2026-07-03 | GOSD04 | V50-11C(10) | PQ3-Week1 | WT-26-0095 | TRUE | WATER SYSTEM (B10) | Building 10 | After RO (Before EDI) (B10) | RO water | 2026-07-03 | 2026-07-06 | 0 | 0 | 0 |  |  | 500 | PASSED | FALSE |  | synced
2026-07-03 | GOSD05 | V50-39(10) | PQ3-Week1 | WT-26-0095 | TRUE | WATER SYSTEM (B10) | Building 10 | After EDI (B10) | PW | 2026-07-03 | 2026-07-06 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-07-03 | GOSD08 | SV117.01 | PQ3-Week1 | WT-26-0095 | TRUE | WATER SYSTEM (B10) | Building 10 | Return loop (B10) | PW | 2026-07-03 | 2026-07-06 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-07-03 | OSD06 | DV116.18 | PQ3-Week1 | WT-26-0095 | TRUE | 10-3-111 | Building 10 | WET GRANULATION-5 | PW | 2026-07-03 | 2026-07-06 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-07-03 | OSD07 | DV116.16 | PQ3-Week1 | WT-26-0095 | TRUE | 10-3-107 | Building 10 | WET GRANULATION-2 | PW | 2026-07-03 | 2026-07-06 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-07-03 | OSD08 | SV116.11 | PQ3-Week1 | WT-26-0095 | TRUE | 10-3-107 | Building 10 | WET GRANULATION-2 | PW | 2026-07-03 | 2026-07-06 | 1 | 0 | 1 |  |  | 100 | PASSED | FALSE |  | synced
2026-07-03 | OSD09 | DV116.14 | PQ3-Week1 | WT-26-0095 | TRUE | 10-3-086 | Building 10 | TOOL WASHING | PW | 2026-07-03 | 2026-07-06 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-07-03 | OSD10 | SV116.09 | PQ3-Week1 | WT-26-0095 | TRUE | 10-3-078 | Building 10 | WASHING | PW | 2026-07-03 | 2026-07-06 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-07-03 | OSD11 | DV116.13 | PQ3-Week1 | WT-26-0095 | TRUE | 10-3-078 | Building 10 | WASHING | PW | 2026-07-03 | 2026-07-06 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-07-03 | OSD12 | DV116.12 | PQ3-Week1 | WT-26-0095 | TRUE | 10-3-078 | Building 10 | WASHING | PW | 2026-07-03 | 2026-07-06 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-07-03 | OSD27 | DV116.17 | PQ3-Week1 | WT-26-0095 | TRUE | 10-3-117 | Building 10 | IPQC-2 | PW | 2026-07-03 | 2026-07-06 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-07-03 | OSD28 | DV116.15 | PQ3-Week1 | WT-26-0095 | TRUE | 10-3-104 | Building 10 | BINDER PREPARATION | PW | 2026-07-03 | 2026-07-06 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-07-07 | GOLD05 | SV133.01 | PQ3-Week2 | WT-26-0096 | TRUE | WATER SYSTEM (B12) | Building 12 | After Storage tank (B12) | PW | 2026-07-08 | 2026-07-11 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-07-07 | GOLD06 | SV135.02 | PQ3-Week2 | WT-26-0096 | TRUE | WATER SYSTEM (B12) | Building 12 | After UV (B12) | PW | 2026-07-08 | 2026-07-11 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-07-07 | GOLD07 | SV137.01 | PQ3-Week2 | WT-26-0096 | TRUE | WATER SYSTEM (B12) | Building 12 | Return loop (B12) | PW | 2026-07-08 | 2026-07-11 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-07-07 | OLD03 | SV136.12 | PQ3-Week2 | WT-26-0096 | TRUE | 12-2-036 | Building 12 | CIP 1 | PW | 2026-07-08 | 2026-07-11 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-07-07 | OLD04 | SV136.07 | PQ3-Week2 | WT-26-0096 | TRUE | 12-2-034 | Building 12 | SYRUP PREPARATION | PW | 2026-07-08 | 2026-07-11 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-07-07 | OLD05 | SV136.06 | PQ3-Week2 | WT-26-0096 | TRUE | 12-2-034 | Building 12 | SYRUP PREPARATION | PW | 2026-07-08 | 2026-07-11 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-07-07 | OLD12 | SV136.03 | PQ3-Week2 | WT-26-0096 | TRUE | 12-2-032 | Building 12 | CAMPHORATED OPIUM TINCTURE | PW | 2026-07-08 | 2026-07-11 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-07-07 | OLD13 | SV136.05 | PQ3-Week2 | WT-26-0096 | TRUE | 12-2-032 | Building 12 | CAMPHORATED OPIUM TINCTURE | PW | 2026-07-08 | 2026-07-11 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-07-07 | OLD14 | SV136.04 | PQ3-Week2 | WT-26-0096 | TRUE | 12-2-030 | Building 12 | OPIUM TINCTURE | PW | 2026-07-08 | 2026-07-11 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-07-07 | OLD15 | DV136.02 | PQ3-Week2 | WT-26-0096 | TRUE | 12-2-028 | Building 12 | ALCOHOL STORAGE | PW | 2026-07-08 | 2026-07-11 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-07-07 | OLD31 | DV136.07 | PQ3-Week2 | WT-26-0096 | TRUE | 12-3-039 | Building 12 | INSTRUMENT 7 | PW | 2026-07-08 | 2026-07-11 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-07-07 | OLD01 | DV136.17 | Speacial |  | FALSE | 12-2-065 | Building 12 | WASHING | PW | 2026-07-08 | 2026-07-11 | 8 | 9 | 9 |  |  | 100 | PASSED | FALSE
2026-07-06 | OCL13 | SV126.19 | PQ3-Week2 | WT-26-0097 | TRUE | 16-3-087 | Building 16 | CIP 2 (EQUIPMENT REQUIREMENT) | PW | 2026-07-08 | 2026-07-11 | 208 | 118 | 163 | IR: 1100003933 |  | 100 | NOT-PASSED | FALSE |  | synced
2026-07-06 | OCL15 | SV126.14 | PQ3-Week2 | WT-26-0097 | TRUE | 16-3-073 | Building 16 | MFG 4 (400L) | PW | 2026-07-08 | 2026-07-11 | 298 | 116 | 207 | IR: 1100003933 |  | 100 | NOT-PASSED | FALSE |  | synced
2026-07-07 | GOCL05 | SV123.01 | PQ3-Week2 | WT-26-0098 | TRUE | WATER SYSTEM (B16) | Building 16 | After Storage tank (B16) | PW | 2026-07-08 | 2026-07-11 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-07-07 | GOCL07 | SV125.02 | PQ3-Week2 | WT-26-0098 | TRUE | WATER SYSTEM (B16) | Building 16 | After UV (B16) | PW | 2026-07-08 | 2026-07-11 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-07-07 | GOCL08 | SV127.01 | PQ3-Week2 | WT-26-0098 | TRUE | WATER SYSTEM (B16) | Building 16 | Return loop (B16) | PW | 2026-07-08 | 2026-07-11 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-07-07 | OCL09 | DV126.10 | PQ3-Week2 | WT-26-0098 | TRUE | 16-3-069 | Building 16 | MFG 2 | PW | 2026-07-08 | 2026-07-11 | 1 | 0 | 1 |  |  | 100 | PASSED | FALSE |  | synced
2026-07-07 | OCL10 | DV126.06 | PQ3-Week2 | WT-26-0098 | TRUE | 16-3-069 | Building 16 | MFG 2 | PW | 2026-07-08 | 2026-07-11 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-07-07 | OCL11 | SV126.10 | PQ3-Week2 | WT-26-0098 | TRUE | 16-3-071 | Building 16 | MFG 3 (1200L) | PW | 2026-07-08 | 2026-07-11 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-07-07 | OCL12 | SV126.09 | PQ3-Week2 | WT-26-0098 | TRUE | 16-3-071 | Building 16 | MFG 3 (5000L) | PW | 2026-07-08 | 2026-07-11 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-07-07 | OCL19 | DV126.07 | PQ3-Week2 | WT-26-0098 | TRUE | 16-3-077 | Building 16 | MFG 6 | PW | 2026-07-08 | 2026-07-11 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-07-07 | OCL18 | DV126.08 | PQ3-Week2 | WT-26-0098 | TRUE | 16-3-077 | Building 16 | MFG 6 | PW | 2026-07-08 | 2026-07-11 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-07-10 | GOSD06 | SV113.01 | PQ3-Week2 | WT-26-0099 | TRUE | WATER SYSTEM (B10) | Building 10 | After Storage tank (B10) | PW | 2026-07-10 | 2026-07-13 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-07-10 | GOSD07 | SV115.02 | PQ3-Week2 | WT-26-0099 | TRUE | WATER SYSTEM (B10) | Building 10 | After UV (B10) | PW | 2026-07-10 | 2026-07-13 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-07-10 | GOSD08 | SV117.01 | PQ3-Week2 | WT-26-0099 | TRUE | WATER SYSTEM (B10) | Building 10 | Return loop (B10) | PW | 2026-07-10 | 2026-07-13 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-07-10 | OSD22 | SV116.05 | PQ3-Week2 | WT-26-0099 | TRUE | 10-3-062 | Building 10 | COATING ROOM-3 | PW | 2026-07-10 | 2026-07-13 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-07-10 | OSD23 | SV116.04 | PQ3-Week2 | WT-26-0099 | TRUE | 10-3-061 | Building 10 | COATING ROOM-2 | PW | 2026-07-10 | 2026-07-13 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-07-10 | OSD24 | DV116.09 | PQ3-Week2 | WT-26-0099 | TRUE | 10-3-060 | Building 10 | COATING SOLUTION PREP.-2 | PW | 2026-07-10 | 2026-07-13 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-07-10 | OSD25 | DV116.08 | PQ3-Week2 | WT-26-0099 | TRUE | 10-3-059 | Building 10 | COATING SOLUTION PREP.-1 | PW | 2026-07-10 | 2026-07-13 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-07-10 | OSD26 | SV116.03 | PQ3-Week2 | WT-26-0099 | TRUE | 10-3-058 | Building 10 | COATING ROOM-1 | PW | 2026-07-10 | 2026-07-13 | 1 | 0 | 1 |  |  | 100 | PASSED | FALSE |  | synced
2026-07-10 | OSD29 | SV116.08 | PQ3-Week2 | WT-26-0099 | TRUE | 10-3-067 | Building 10 | COATING ROOM-6 | PW | 2026-07-10 | 2026-07-13 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-07-10 | OSD30 | DV116.11 | PQ3-Week2 | WT-26-0099 | TRUE | 10-3-066 | Building 10 | COATING SOLUTION PREP.-4 | PW | 2026-07-10 | 2026-07-13 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-07-10 | OSD31 | DV116.10 | PQ3-Week2 | WT-26-0099 | TRUE | 10-3-065 | Building 10 | COATING SOLUTION PREP.-3 | PW | 2026-07-10 | 2026-07-13 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-07-10 | OSD32 | SV116.07 | PQ3-Week2 | WT-26-0099 | TRUE | 10-3-064 | Building 10 | COATING ROOM-5 | PW | 2026-07-10 | 2026-07-13 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-07-10 | OSD33 | SV116.06 | PQ3-Week2 | WT-26-0099 | TRUE | 10-3-063 | Building 10 | COATING ROOM-4 | PW | 2026-07-10 | 2026-07-13 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-07-10 | OSD36 | DV116.03 | PQ3-Week2 | WT-26-0099 | TRUE | 10-2-034 | Building 10 | SAMPLE PREPARATION | PW | 2026-07-10 | 2026-07-13 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-07-10 | OSD37 | DV116.06 | PQ3-Week2 | WT-26-0099 | TRUE | 10-2-034 | Building 10 | SAMPLE PREPARATION | PW | 2026-07-10 | 2026-07-13 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-07-10 | OSD38 | DV116.07 | PQ3-Week2 | WT-26-0099 | TRUE | 10-2-032 | Building 10 | GLASS-WARE WASHING | PW | 2026-07-10 | 2026-07-13 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-07-10 | OSD39 | DV116.05 | PQ3-Week2 | WT-26-0099 | TRUE | 10-2-032 | Building 10 | GLASS-WARE WASHING | PW | 2026-07-10 | 2026-07-13 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-07-10 | OSD40 | DV116.04 | PQ3-Week2 | WT-26-0099 | TRUE | 10-2-037 | Building 10 | SKID FOR BIN WASHING-1 | PW | 2026-07-10 | 2026-07-13 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-07-10 | BU19-14 | SV-14 | PQ3-Week2 | WT-26-0100 | TRUE | PROCESS WATER (B19) | Building 19 | AFTER RO SYSTEM NO.12 SV14 | PRW | 2026-07-10 | 2026-07-13 | 1 | 1 | 1 |  |  | 500 | PASSED | FALSE |  | synced
2026-07-10 | GOLD07 | SV137.01 | Speacial |  | FALSE | WATER SYSTEM (B12) | Building 12 | Return loop (B12) | PW | 2026-07-11 | 2026-07-14 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE
2026-07-10 | OLD01 | DV136.17 | Speacial |  | FALSE | 12-2-065 | Building 12 | WASHING | PW | 2026-07-11 | 2026-07-14 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE
2026-07-10 | OLD20 | DV136.16 | Speacial |  | FALSE | 12-1-064 | Building 12 | WASHING | PW | 2026-07-11 | 2026-07-14 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE
2026-07-10 | OLD25 | DV136.12 | Speacial |  | FALSE | 12-3-056 | Building 12 | MEDIA PREPARATION | PW | 2026-07-11 | 2026-07-14 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE
2026-07-13 | GOLD07 | SV137.01 | Speacial |  | FALSE | WATER SYSTEM (B12) | Building 12 | Return loop (B12) | PW | 2026-07-14 | 2026-07-17 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE
2026-07-13 | OLD01 | DV136.17 | Speacial |  | FALSE | 12-2-065 | Building 12 | WASHING | PW | 2026-07-14 | 2026-07-17 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE
2026-07-13 | OLD20 | DV136.16 | Speacial |  | FALSE | 12-1-064 | Building 12 | WASHING | PW | 2026-07-14 | 2026-07-17 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE
2026-07-13 | OLD25 | DV136.12 | Speacial |  | FALSE | 12-3-056 | Building 12 | MEDIA PREPARATION | PW | 2026-07-14 | 2026-07-17 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE
2026-07-14 | GOLD01 | VB-05 (12) | PQ3-Week3 | WT-26-0101 | TRUE | WATER SYSTEM (B12) | Building 12 | After Chlorine circulation tank | PRW | 2026-07-14 | 2026-07-17 | 0 | 0 | 0 |  |  | 500 | PASSED | FALSE |  | synced
2026-07-14 | GOLD02 | V50-61 (12) | PQ3-Week3 | WT-26-0101 | TRUE | WATER SYSTEM (B12) | Building 12 | After Cartridge filter 5 µm (B12) | PRW | 2026-07-14 | 2026-07-17 | 69 | 133 | 101 |  |  | 500 | PASSED | FALSE |  | synced
2026-07-14 | GOLD03 | V50-11C (12) | PQ3-Week3 | WT-26-0101 | TRUE | WATER SYSTEM (B12) | Building 12 | After RO (Before EDI) (B12) | RO water | 2026-07-14 | 2026-07-17 | 0 | 0 | 0 |  |  | 500 | PASSED | FALSE |  | synced
2026-07-14 | GOLD04 | V50-39 (12) | PQ3-Week3 | WT-26-0101 | TRUE | WATER SYSTEM (B12) | Building 12 | After EDI (B12) | PW | 2026-07-14 | 2026-07-17 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-07-14 | GOLD07 | SV137.01 | PQ3-Week3 | WT-26-0101 | TRUE | WATER SYSTEM (B12) | Building 12 | Return loop (B12) | PW | 2026-07-14 | 2026-07-17 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-07-14 | OLD01 | DV136.17 | PQ3-Week3 | WT-26-0101 | TRUE | 12-2-065 | Building 12 | WASHING | PW | 2026-07-14 | 2026-07-17 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-07-14 | OLD02 | SV136.16 | PQ3-Week3 | WT-26-0101 | TRUE | 12-2-057 | Building 12 | CIP 2 | PW | 2026-07-14 | 2026-07-17 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-07-14 | OLD10 | SV136.15 | PQ3-Week3 | WT-26-0101 | TRUE | 12-2-055 | Building 12 | CIP 3 | PW | 2026-07-14 | 2026-07-17 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-07-14 | OLD17 | DV136.03 | PQ3-Week3 | WT-26-0101 | TRUE | 12-2-053 | Building 12 | IPQC | PW | 2026-07-14 | 2026-07-17 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-07-14 | OLD19 | DV136.01 | PQ3-Week3 | WT-26-0101 | TRUE | 12-1-035 | Building 12 | SUGAR TRANSFERRING | PW | 2026-07-14 | 2026-07-17 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-07-14 | OLD20 | DV136.16 | PQ3-Week3 | WT-26-0101 | TRUE | 12-1-064 | Building 12 | WASHING | PW | 2026-07-14 | 2026-07-17 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-07-14 | OLD34 | DV136.04 | PQ3-Week3 | WT-26-0101 | TRUE | 12-2-077 | Building 12 | WATER SYSTEM ROOM | PW | 2026-07-14 | 2026-07-17 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-07-14 | GOCL01 | VB-05 (16) | PQ3-Week3 | WT-26-0102 | TRUE | WATER SYSTEM (B16) | Building 16 | After Chlorine circulation tank (B16) | PRW | 2026-07-14 | 2026-07-17 | 1 | 0 | 1 |  |  | 500 | PASSED | FALSE |  | synced
2026-07-14 | GOCL02 | V50-61 (16) | PQ3-Week3 | WT-26-0102 | TRUE | WATER SYSTEM (B16) | Building 16 | After Cartridge filter 5 µm (B16) | PRW | 2026-07-14 | 2026-07-17 | 64 | 30 | 47 |  |  | 500 | PASSED | FALSE |  | synced
2026-07-14 | GOCL03 | V50-11C (16) | PQ3-Week3 | WT-26-0102 | TRUE | WATER SYSTEM (B16) | Building 16 | After RO (Before EDI) (B16) | RO water | 2026-07-14 | 2026-07-17 | 0 | 0 | 0 |  |  | 500 | PASSED | FALSE |  | synced
2026-07-14 | GOCL04 | V50-39 (16) | PQ3-Week3 | WT-26-0102 | TRUE | WATER SYSTEM (B16) | Building 16 | After EDI (B16) | PW | 2026-07-14 | 2026-07-17 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-07-14 | GOCL08 | SV127.01 | PQ3-Week3 | WT-26-0102 | TRUE | WATER SYSTEM (B16) | Building 16 | Return loop (B16) | PW | 2026-07-14 | 2026-07-17 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-07-14 | OCL06 | SV126.06 | PQ3-Week3 | WT-26-0102 | TRUE | 16-3-067 | Building 16 | MFG 1 | PW | 2026-07-14 | 2026-07-17 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-07-14 | OCL07 | SV126.21 | PQ3-Week3 | WT-26-0102 | TRUE | 16-3-090 | Building 16 | CIP 1 (EQUIPMENT REQUIREMENT) | PW | 2026-07-14 | 2026-07-17 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-07-14 | OCL08 | DV126.09 | PQ3-Week3 | WT-26-0102 | TRUE | 16-3-090 | Building 16 | CIP 1 (ZINK WASHING) | PW | 2026-07-14 | 2026-07-17 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-07-14 | OCL16 | SV126.18 | PQ3-Week3 | WT-26-0102 | TRUE | 16-3-085 | Building 16 | CIP 3 (EQUIPMENT REQUIREMENT) | PW | 2026-07-14 | 2026-07-17 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-07-14 | OCL20 | SV126.05 | PQ3-Week3 | WT-26-0102 | TRUE | 16-3-049 | Building 16 | LINEN WASHING | PW | 2026-07-14 | 2026-07-17 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-07-14 | OCL24 | DV126.04 | PQ3-Week3 | WT-26-0102 | TRUE | 16-2-010 | Building 16 | WATER SYSTEM (PW) | PW | 2026-07-14 | 2026-07-17 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-07-16 | OCL13 | SV126.19 | PQ3-Week3 | WT-26-0103 | TRUE | 16-3-087 | Building 16 | CIP 2 (EQUIPMENT REQUIREMENT) | PW | 2026-07-17 | 2026-07-20 | 2 | 0 | 1 |  |  | 100 | PASSED | FALSE |  | synced
2026-07-16 | OCL15 | SV126.14 | PQ3-Week3 | WT-26-0103 | TRUE | 16-3-073 | Building 16 | MFG 4 (400L) | PW | 2026-07-17 | 2026-07-20 | 2 | 0 | 1 |  |  | 100 | PASSED | FALSE |  | synced
2026-07-17 | BU19-14 | SV-14 | PQ3-Week3 | WT-26-0104 | TRUE | PROCESS WATER (B19) | Building 19 | AFTER RO SYSTEM NO.12 SV14 | PRW | 2026-07-17 | 2026-07-20 | 328 | 448 | 388 |  |  | 500 | PASSED | FALSE |  | synced
2026-07-17 | GOSD01 | VB-05(10) | PQ3-Week3 | WT-26-0105 | TRUE | WATER SYSTEM (B10) | Building 10 | After Chlorine circulation tank (B10) | PRW | 2026-07-17 | 2026-07-20 | 8 | 112 | 60 |  |  | 500 | PASSED | FALSE |  | synced
2026-07-17 | GOSD03 | V50-61(10) | PQ3-Week3 | WT-26-0105 | TRUE | WATER SYSTEM (B10) | Building 10 | After Cartridge filter 5 µm (B10) | PRW | 2026-07-17 | 2026-07-20 | 258 | 183 | 221 |  |  | 500 | PASSED | FALSE |  | synced
2026-07-17 | GOSD04 | V50-11C(10) | PQ3-Week3 | WT-26-0105 | TRUE | WATER SYSTEM (B10) | Building 10 | After RO (Before EDI) (B10) | RO water | 2026-07-17 | 2026-07-20 | 0 | 0 | 0 |  |  | 500 | PASSED | FALSE |  | synced
2026-07-17 | GOSD05 | V50-39(10) | PQ3-Week3 | WT-26-0105 | TRUE | WATER SYSTEM (B10) | Building 10 | After EDI (B10) | PW | 2026-07-17 | 2026-07-20 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-07-17 | GOSD08 | SV117.01 | PQ3-Week3 | WT-26-0105 | TRUE | WATER SYSTEM (B10) | Building 10 | Return loop (B10) | PW | 2026-07-17 | 2026-07-20 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-07-17 | OSD13 | DV116.25 | PQ3-Week3 | WT-26-0105 | TRUE | 10-3-171 | Building 10 | TOOL WASHING-P | PW | 2026-07-17 | 2026-07-20 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-07-17 | OSD14 | DV116.24 | PQ3-Week3 | WT-26-0105 | TRUE | 10-3-163 | Building 10 | WET GRANULATION 1-P | PW | 2026-07-17 | 2026-07-20 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-07-17 | OSD15 | DV116.23 | PQ3-Week3 | WT-26-0105 | TRUE | 10-3-159 | Building 10 | BINDER PREPARATION-P | PW | 2026-07-17 | 2026-07-20 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-07-17 | OSD16 | DV116.21 | PQ3-Week3 | WT-26-0105 | TRUE | 10-3-152 | Building 10 | WASHING-P | PW | 2026-07-17 | 2026-07-20 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-07-17 | OSD17 | DV116.22 | PQ3-Week3 | WT-26-0105 | TRUE | 10-3-152 | Building 10 | WASHING-P | PW | 2026-07-17 | 2026-07-20 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-07-17 | OSD18 | SV116.13 | PQ3-Week3 | WT-26-0105 | TRUE | 10-3-152 | Building 10 | WASHING-P | PW | 2026-07-17 | 2026-07-20 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-07-17 | OSD19 | DV116.20 | PQ3-Week3 | WT-26-0105 | TRUE | 10-3-149 | Building 10 | IPQC-1-P | PW | 2026-07-17 | 2026-07-20 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-07-17 | OSD20 | DV116.19 | PQ3-Week3 | WT-26-0105 | TRUE | 10-3-143 | Building 10 | COATING SOLUTION PREP.-P | PW | 2026-07-17 | 2026-07-20 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-07-17 | OSD21 | SV116.12 | PQ3-Week3 | WT-26-0105 | TRUE | 10-3-144 | Building 10 | COATING-P | PW | 2026-07-17 | 2026-07-20 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-07-17 | OSD41 | DV116.02 | PQ3-Week3 | WT-26-0105 | TRUE | 10-1-115 | Building 10 | WASHING | PW | 2026-07-17 | 2026-07-20 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-07-17 | OSD42 | DV116.01 | PQ3-Week3 | WT-26-0105 | TRUE | 10-1-057 | Building 10 | WASHING-P | PW | 2026-07-17 | 2026-07-20 | 3 | 0 | 2 |  |  | 100 | PASSED | FALSE |  | synced
2026-07-20 | GOLD07 | SV137.01 | Speacial | WT-26-0106 | TRUE | WATER SYSTEM (B12) | Building 12 | Return loop (B12) | PW | 2026-07-21 | 2026-07-24 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-07-20 | OLD06 | SV136.09 | Speacial | WT-26-0106 | TRUE | 12-2-039 | Building 12 | MFG 1 | PW | 2026-07-21 | 2026-07-24 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-07-21 | GOLD05 | SV133.01 | PQ3-Week4 | WT-26-0107 | TRUE | WATER SYSTEM (B12) | Building 12 | After Storage tank (B12) | PW | 2026-07-21 | 2026-07-24 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-07-21 | GOLD06 | SV135.02 | PQ3-Week4 | WT-26-0107 | TRUE | WATER SYSTEM (B12) | Building 12 | After UV (B12) | PW | 2026-07-21 | 2026-07-24 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-07-21 | GOLD07 | SV137.01 | PQ3-Week4 | WT-26-0107 | TRUE | WATER SYSTEM (B12) | Building 12 | Return loop (B12) | PW | 2026-07-21 | 2026-07-24 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-07-21 | OLD06 | SV136.09 | PQ3-Week4 | WT-26-0107 | TRUE | 12-2-039 | Building 12 | MFG 1 | PW | 2026-07-21 | 2026-07-24 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-07-21 | OLD07 | SV136.10 | PQ3-Week4 | WT-26-0107 | TRUE | 12-2-041 | Building 12 | MFG 2 | PW | 2026-07-21 | 2026-07-24 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-07-21 | OLD08 | SV136.11 | PQ3-Week4 | WT-26-0107 | TRUE | 12-2-043 | Building 12 | MFG 3 | PW | 2026-07-21 | 2026-07-24 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-07-21 | OLD11 | SV136.08 | PQ3-Week4 | WT-26-0107 | TRUE | 12-2-043 | Building 12 | MFG 3 | PW | 2026-07-21 | 2026-07-24 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-07-21 | OLD16 | SV136.14 | PQ3-Week4 | WT-26-0107 | TRUE | 12-2-045 | Building 12 | MFG 4 | PW | 2026-07-21 | 2026-07-24 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-07-21 | OLD18 | SV136.02 | PQ3-Week4 | WT-26-0107 | TRUE | 12-2-024 | Building 12 | LIQUORICE EXTRACT | PW | 2026-07-21 | 2026-07-24 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-07-21 | OLD32 | DV136.08 | PQ3-Week4 | WT-26-0107 | TRUE | 12-3-042 | Building 12 | SAMPLE PREPARATION | PW | 2026-07-21 | 2026-07-24 | 414 | 511 | 463 | IR: 1100003940 |  | 100 | NOT-PASSED | FALSE |  | synced
2026-07-21 | OLD33 | DV136.09 | PQ3-Week4 | WT-26-0107 | TRUE | 12-3-042 | Building 12 | SAMPLE PREPARATION | PW | 2026-07-21 | 2026-07-24 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-07-21 | GOCL05 | SV123.01 | PQ3-Week4 | WT-26-0108 | TRUE | WATER SYSTEM (B16) | Building 16 | After Storage tank (B16) | PW | 2026-07-21 | 2026-07-24 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-07-21 | GOCL07 | SV125.02 | PQ3-Week4 | WT-26-0108 | TRUE | WATER SYSTEM (B16) | Building 16 | After UV (B16) | PW | 2026-07-21 | 2026-07-24 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-07-21 | GOCL08 | SV127.01 | PQ3-Week4 | WT-26-0108 | TRUE | WATER SYSTEM (B16) | Building 16 | Return loop (B16) | PW | 2026-07-21 | 2026-07-24 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-07-21 | OCL14 | DV126.11 | PQ3-Week4 | WT-26-0108 | TRUE | 16-3-073 | Building 16 | MFG 4 (5000L) | PW | 2026-07-21 | 2026-07-24 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-07-21 | OCL17 | SV126.15 | PQ3-Week4 | WT-26-0108 | TRUE | 16-3-075 | Building 16 | MFG 5 PROCESS (2000L) | PW | 2026-07-21 | 2026-07-24 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-07-21 | OCL21 | DV126.05 | PQ3-Week4 | WT-26-0108 | TRUE | 16-3-054 | Building 16 | WASHING | PW | 2026-07-21 | 2026-07-24 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-07-21 | OCL23 | SV126.04 | PQ3-Week4 | WT-26-0108 | TRUE | 16-2-010 | Building 16 | WATER SYSTEM (PSG) | PW | 2026-07-21 | 2026-07-24 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-07-22 | GOLD07 | SV137.01 | Speacial | WT-26-0109 | TRUE | WATER SYSTEM (B12) | Building 12 | Return loop (B12) | PW | 2026-07-23 | 2026-07-27 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-07-22 | OLD09 | SV136.13 | Speacial | WT-26-0109 | TRUE | 12-2-043 | Building 12 | MFG 3 | PW | 2026-07-23 | 2026-07-27 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-07-23 | GOLD07 | SV137.01 | Speacial | WT-26-0110 | TRUE | WATER SYSTEM (B12) | Building 12 | Return loop (B12) | PW | 2026-07-23 | 2026-07-27 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-07-23 | OLD02 | SV136.16 | Speacial | WT-26-0110 | TRUE | 12-2-057 | Building 12 | CIP 2 | PW | 2026-07-23 | 2026-07-27 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-07-23 | OLD06 | SV136.09 | Speacial | WT-26-0113 | TRUE | 12-2-039 | Building 12 | MFG 1 | PW | 2026-07-23 | 2026-07-27 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-07-24 | GOLD07 | SV137.01 | Speacial | WT-26-0111 | TRUE | WATER SYSTEM (B12) | Building 12 | Return loop (B12) | PW | 2026-07-24 | 2026-07-27 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-07-24 | OLD10 | SV136.15 | Speacial | WT-26-0111 | TRUE | 12-2-055 | Building 12 | CIP 3 | PW | 2026-07-24 | 2026-07-27 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-07-24 | OLD09 | SV136.13 | Speacial | WT-26-0114 | TRUE | 12-2-043 | Building 12 | MFG 3 | PW | 2026-07-24 |  | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-07-24 | GOSD06 | SV113.01 | PQ3-Week4 | WT-26-0112 | TRUE | WATER SYSTEM (B10) | Building 10 | After Storage tank (B10) | PW | 2026-07-24 | 2026-07-27 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-07-24 | GOSD07 | SV115.02 | PQ3-Week4 | WT-26-0112 | TRUE | WATER SYSTEM (B10) | Building 10 | After UV (B10) | PW | 2026-07-24 | 2026-07-27 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-07-24 | GOSD08 | SV117.01 | PQ3-Week4 | WT-26-0112 | TRUE | WATER SYSTEM (B10) | Building 10 | Return loop (B10) | PW | 2026-07-24 | 2026-07-27 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-07-24 | OSD01 | SV116.15 | PQ3-Week4 | WT-26-0112 | TRUE | 10-4-012 | Building 10 | CIP SKID-1 FOR BIN WASHING-1 | PW | 2026-07-24 | 2026-07-27 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-07-24 | OSD02 | SV116.16 | PQ3-Week4 | WT-26-0112 | TRUE | 10-4-012 | Building 10 | WIP SKID-3 FOR GRANULATION POTENT | PW | 2026-07-24 | 2026-07-27 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-07-24 | OSD03 | SV116.17 | PQ3-Week4 | WT-26-0112 | TRUE | 10-4-012 | Building 10 | CIP SKID-2 FOR BIN WASHING-1 | PW | 2026-07-24 | 2026-07-27 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-07-24 | OSD04 | SV116.18 | PQ3-Week4 | WT-26-0112 | TRUE | 10-4-012 | Building 10 | WIP SKID-1 FOR GRANULATION NON POTENT | PW | 2026-07-24 | 2026-07-27 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-07-24 | OSD05 | SV116.19 | PQ3-Week4 | WT-26-0112 | TRUE | 10-4-012 | Building 10 | WIP SKID-2 FOR GRANULATION NON POTENT | PW | 2026-07-24 | 2026-07-27 | 7 | 8 | 8 |  |  | 100 | PASSED | FALSE |  | synced
2026-07-24 | OSD34 | SV116.02 | PQ3-Week4 | WT-26-0112 | TRUE | 10-2-037 | Building 10 | SKID FOR BIN WASHING-2 | PW | 2026-07-24 | 2026-07-27 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-07-24 | OSD35 | SV116.01 | PQ3-Week4 | WT-26-0112 | TRUE | 10-2-021 | Building 10 | INSTRUMENT-1 | PW | 2026-07-24 | 2026-07-27 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-07-24 | OSD43 | DV116.26 | PQ3-Week4 | WT-26-0112 | TRUE | 10-4-015 | Building 10 | WATER SYSTEM ROOM | PW | 2026-07-24 | 2026-07-27 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-07-27 | GOSD01 | VB-05(10) | Speacial | WT-26-0115 | TRUE | WATER SYSTEM (B10) | Building 10 | After Chlorine circulation tank (B10) | PRW | 2026-07-27 | 2026-07-31 | 212 | 236 | 224 |  |  | 500 | PASSED | FALSE |  | synced
2026-07-27 | GOSD03 | V50-61(10) | Speacial | WT-26-0115 | TRUE | WATER SYSTEM (B10) | Building 10 | After Cartridge filter 5 µm (B10) | PRW | 2026-07-27 | 2026-07-31 | 191 | 176 | 184 |  |  | 500 | PASSED | FALSE |  | synced
2026-07-27 | GOSD04 | V50-11C(10) | Speacial | WT-26-0115 | TRUE | WATER SYSTEM (B10) | Building 10 | After RO (Before EDI) (B10) | RO water | 2026-07-27 | 2026-07-31 | 0 | 0 | 0 |  |  | 500 | PASSED | FALSE |  | synced
2026-07-27 | GOSD05 | V50-39(10) | Speacial | WT-26-0115 | TRUE | WATER SYSTEM (B10) | Building 10 | After EDI (B10) | PW | 2026-07-27 | 2026-07-31 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-07-27 | GOLD01 | VB-05 (12) | Speacial | WT-26-0116 | TRUE | WATER SYSTEM (B12) | Building 12 | After Chlorine circulation tank | PRW | 2026-07-27 | 2026-07-31 | 0 | 0 | 0 |  |  | 500 | PASSED | FALSE |  | synced
2026-07-27 | GOLD02 | V50-61 (12) | Speacial | WT-26-0116 | TRUE | WATER SYSTEM (B12) | Building 12 | After Cartridge filter 5 µm (B12) | PRW | 2026-07-27 | 2026-07-31 | 31 | 39 | 35 |  |  | 500 | PASSED | FALSE |  | synced
2026-07-27 | GOLD03 | V50-11C (12) | Speacial | WT-26-0116 | TRUE | WATER SYSTEM (B12) | Building 12 | After RO (Before EDI) (B12) | RO water | 2026-07-27 | 2026-07-31 | 0 | 0 | 0 |  |  | 500 | PASSED | FALSE |  | synced
2026-07-27 | GOLD04 | V50-39 (12) | Speacial | WT-26-0116 | TRUE | WATER SYSTEM (B12) | Building 12 | After EDI (B12) | PW | 2026-07-27 | 2026-07-31 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-07-27 | OLD09 | SV136.13 | Speacial | WT-26-0116 | TRUE | 12-2-043 | Building 12 | MFG 3 | PW | 2026-07-27 | 2026-07-31 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-07-27 | GOCL01 | VB-05 (16) | Speacial | WT-26-0117 | TRUE | WATER SYSTEM (B16) | Building 16 | After Chlorine circulation tank (B16) | PRW | 2026-07-27 | 2026-07-31 | 254 | 210 | 232 |  |  | 500 | PASSED | FALSE |  | synced
2026-07-27 | GOCL02 | V50-61 (16) | Speacial | WT-26-0117 | TRUE | WATER SYSTEM (B16) | Building 16 | After Cartridge filter 5 µm (B16) | PRW | 2026-07-27 | 2026-07-31 | 140 | 157 | 149 |  |  | 500 | PASSED | FALSE |  | synced
2026-07-27 | GOCL03 | V50-11C (16) | Speacial | WT-26-0117 | TRUE | WATER SYSTEM (B16) | Building 16 | After RO (Before EDI) (B16) | RO water | 2026-07-27 | 2026-07-31 | 0 | 0 | 0 |  |  | 500 | PASSED | FALSE |  | synced
2026-07-27 | GOCL04 | V50-39 (16) | Speacial | WT-26-0117 | TRUE | WATER SYSTEM (B16) | Building 16 | After EDI (B16) | PW | 2026-07-27 | 2026-07-31 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-07-31 | GOSD08 | SV117.01 | Speacial | WT-26-0118 | TRUE | WATER SYSTEM (B10) | Building 10 | Return loop (B10) | PW | 2026-07-31 | 2026-08-03 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-07-31 | OSD28 | DV116.15 | Speacial | WT-26-0118 | TRUE | 10-3-104 | Building 10 | BINDER PREPARATION | PW | 2026-07-31 | 2026-08-03 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-07-31 | GOLD07 | SV137.01 | Speacial | WT-26-0119 | TRUE | WATER SYSTEM (B12) | Building 12 | Return loop (B12) | PW | 2026-07-31 | 2026-08-03 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-07-31 | GOCL08 | SV127.01 | Speacial | WT-26-0120 | TRUE | WATER SYSTEM (B16) | Building 16 | Return loop (B16) | PW | 2026-07-31 | 2026-08-03 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-08-03 | GOLD07 | SV137.01 | Speacial | WT-26-0121 | TRUE | WATER SYSTEM (B12) | Building 12 | Return loop (B12) | PW | 2026-08-04 | 2026-08-07 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-08-04 | GOLD05 | SV133.01 | PQ3-Week1 | WT-26-0122 | TRUE | WATER SYSTEM (B12) | Building 12 | After Storage tank (B12) | PW | 2026-08-04 | 2026-08-07 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-08-04 | GOLD06 | SV135.02 | PQ3-Week1 | WT-26-0122 | TRUE | WATER SYSTEM (B12) | Building 12 | After UV (B12) | PW | 2026-08-04 | 2026-08-07 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-08-04 | GOLD07 | SV137.01 | PQ3-Week1 | WT-26-0122 | TRUE | WATER SYSTEM (B12) | Building 12 | Return loop (B12) | PW | 2026-08-04 | 2026-08-07 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-08-04 | OLD06 | SV136.09 | PQ3-Week1 | WT-26-0122 | TRUE | 12-2-039 | Building 12 | MFG 1 | PW | 2026-08-04 | 2026-08-07 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-08-04 | OLD21 | DV136.15 | PQ3-Week1 | WT-26-0122 | TRUE | 12-3-078 | Building 12 | GLASSWARE WASHING 2 | PW | 2026-08-04 | 2026-08-07 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-08-04 | OLD22 | DV136.13 | PQ3-Week1 | WT-26-0122 | TRUE | 12-3-057 | Building 12 | STERILIZATION | PW | 2026-08-04 | 2026-08-07 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-08-04 | OLD23 | SV136.18 | PQ3-Week1 | WT-26-0122 | TRUE | 12-3-059 | Building 12 | AUTOCLAVE | PW | 2026-08-04 | 2026-08-07 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-08-04 | OLD24 | DV136.11 | PQ3-Week1 | WT-26-0122 | TRUE | 12-3-059 | Building 12 | AUTOCLAVE | PW | 2026-08-04 | 2026-08-07 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-08-04 | OLD25 | DV136.12 | PQ3-Week1 | WT-26-0122 | TRUE | 12-3-056 | Building 12 | MEDIA PREPARATION | PW | 2026-08-04 | 2026-08-07 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-08-04 | OLD26 | DV136.10 | PQ3-Week1 | WT-26-0122 | TRUE | 12-3-056 | Building 12 | MEDIA PREPARATION | PW | 2026-08-04 | 2026-08-07 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-08-04 | OLD27 | DV136.14 | PQ3-Week1 | WT-26-0122 | TRUE | 12-3-074 | Building 12 | DECONTAMINATION | PW | 2026-08-04 | 2026-08-07 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-08-04 | OLD28 | DV136.18 | PQ3-Week1 | WT-26-0122 | TRUE | 12-3-037 | Building 12 | GLASSWARE WASHING 1 | PW | 2026-08-04 | 2026-08-07 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-08-04 | OLD29 | DV136.05 | PQ3-Week1 | WT-26-0122 | TRUE | 12-3-037 | Building 12 | GLASSWARE WASHING 1 | PW | 2026-08-04 | 2026-08-07 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-08-04 | OLD30 | DV136.06 | PQ3-Week1 | WT-26-0122 | TRUE | 12-3-037 | Building 12 | GLASSWARE WASHING 1 | PW | 2026-08-04 | 2026-08-07 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-08-04 | GOCL05 | SV123.01 | PQ3-Week1 | WT-26-0123 | TRUE | WATER SYSTEM (B16) | Building 16 | After Storage tank (B16) | PW | 2026-08-04 | 2026-08-07 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-08-04 | GOCL07 | SV125.02 | PQ3-Week1 | WT-26-0123 | TRUE | WATER SYSTEM (B16) | Building 16 | After UV (B16) | PW | 2026-08-04 | 2026-08-07 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-08-04 | GOCL08 | SV127.01 | PQ3-Week1 | WT-26-0123 | TRUE | WATER SYSTEM (B16) | Building 16 | Return loop (B16) | PW | 2026-08-04 | 2026-08-07 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-08-04 | OCL01 | DV126.02 | PQ3-Week1 | WT-26-0123 | TRUE | 16-1-082 | Building 16 | WASHING | PW | 2026-08-04 | 2026-08-07 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-08-04 | OCL02 | DV126.01 | PQ3-Week1 | WT-26-0123 | TRUE | 16-1-082 | Building 16 | WASHING | PW | 2026-08-04 | 2026-08-07 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-08-04 | OCL03 | SV126.02 | PQ3-Week1 | WT-26-0123 | TRUE | 16-1-098 | Building 16 | CIP/SIP (EQUIPMENT REQUIREMENT – 200L) | PW | 2026-08-04 | 2026-08-07 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-08-04 | OCL04 | DV126.03 | PQ3-Week1 | WT-26-0123 | TRUE | 16-1-098 | Building 16 | CIP/SIP (SINK WASHING) | PW | 2026-08-04 | 2026-08-07 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-08-04 | OCL05 | SV126.01 | PQ3-Week1 | WT-26-0123 | TRUE | 16-1-092 | Building 16 | LINEN WASHING | PW | 2026-08-04 | 2026-08-07 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-08-04 | OCL22 | SV126.03 | PQ3-Week1 | WT-26-0123 | TRUE | 16-2-010 | Building 16 | WATER SYSTEM (WFI) | PW | 2026-08-04 | 2026-08-07 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-08-05 | GOLD07 | SV137.01 | Speacial | WT-26-0124 | TRUE | WATER SYSTEM (B12) | Building 12 | Return loop (B12) | PW | 2026-08-06 | 2026-08-10 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-08-05 | OLD02 | SV136.16 | Speacial | WT-26-0124 | TRUE | 12-2-057 | Building 12 | CIP 2 | PW | 2026-08-06 | 2026-08-10 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-08-05 | OLD10 | SV136.15 | Speacial | WT-26-0124 | TRUE | 12-2-055 | Building 12 | CIP 3 | PW | 2026-08-06 | 2026-08-10 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-08-06 | GOLD07 | SV137.01 | Speacial | WT-26-0125 | TRUE | WATER SYSTEM (B12) | Building 12 | Return loop (B12) | PW | 2026-08-06 | 2026-08-10 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-08-06 | OLD07 | SV136.10 | Speacial | WT-26-0125 | TRUE | 12-2-041 | Building 12 | MFG 2 | PW | 2026-08-06 | 2026-08-10 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-08-07 | GOLD07 | SV137.01 | Speacial | WT-26-0126 | TRUE | WATER SYSTEM (B12) | Building 12 | Return loop (B12) | PW | 2026-08-08 | 2026-08-11 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-08-07 | OLD09 | SV136.13 | Speacial | WT-26-0126 | TRUE | 12-2-043 | Building 12 | MFG 3 | PW | 2026-08-08 | 2026-08-11 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-08-07 | GOSD06 | SV113.01 | PQ3-Week1 | WT-26-0127 | TRUE | WATER SYSTEM (B10) | Building 10 | After Storage tank (B10) | PW | 2026-08-08 | 2026-08-11 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-08-07 | GOSD07 | SV115.02 | PQ3-Week1 | WT-26-0127 | TRUE | WATER SYSTEM (B10) | Building 10 | After UV (B10) | PW | 2026-08-08 | 2026-08-11 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-08-07 | GOSD08 | SV117.01 | PQ3-Week1 | WT-26-0127 | TRUE | WATER SYSTEM (B10) | Building 10 | Return loop (B10) | PW | 2026-08-08 | 2026-08-11 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-08-07 | OSD06 | DV116.18 | PQ3-Week1 | WT-26-0127 | TRUE | 10-3-111 | Building 10 | WET GRANULATION-5 | PW | 2026-08-08 | 2026-08-11 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-08-07 | OSD07 | DV116.16 | PQ3-Week1 | WT-26-0127 | TRUE | 10-3-107 | Building 10 | WET GRANULATION-2 | PW | 2026-08-08 | 2026-08-11 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-08-07 | OSD08 | SV116.11 | PQ3-Week1 | WT-26-0127 | TRUE | 10-3-107 | Building 10 | WET GRANULATION-2 | PW | 2026-08-08 | 2026-08-11 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-08-07 | OSD09 | DV116.14 | PQ3-Week1 | WT-26-0127 | TRUE | 10-3-086 | Building 10 | TOOL WASHING | PW | 2026-08-08 | 2026-08-11 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-08-07 | OSD10 | SV116.09 | PQ3-Week1 | WT-26-0127 | TRUE | 10-3-078 | Building 10 | WASHING | PW | 2026-08-08 | 2026-08-11 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-08-07 | OSD11 | DV116.13 | PQ3-Week1 | WT-26-0127 | TRUE | 10-3-078 | Building 10 | WASHING | PW | 2026-08-08 | 2026-08-11 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-08-07 | OSD12 | DV116.12 | PQ3-Week1 | WT-26-0127 | TRUE | 10-3-078 | Building 10 | WASHING | PW | 2026-08-08 | 2026-08-11 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-08-07 | OSD27 | DV116.17 | PQ3-Week1 | WT-26-0127 | TRUE | 10-3-117 | Building 10 | IPQC-2 | PW | 2026-08-08 | 2026-08-11 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-08-07 | OSD28 | DV116.15 | PQ3-Week1 | WT-26-0127 | TRUE | 10-3-104 | Building 10 | BINDER PREPARATION | PW | 2026-08-08 | 2026-08-11 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-08-07 | BU19-14 | SV14 | PQ3-Week1 | WT-26-0128 | TRUE | B.19 | Building 19 | AFTER RO SYSTEM NO.12 SV14 | PRW | 2026-08-08 | 2026-08-11 | 176 | 206 | 191 |  |  | 500 | PASSED | FALSE |  | synced
2026-08-10 | GOLD07 | SV137.01 | Speacial | WT-26-0129 | TRUE | WATER SYSTEM (B12) | Building 12 | Return loop (B12) | PW | 2026-08-11 | 2026-08-14 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-08-10 | OLD01 | DV136.17 | Speacial | WT-26-0129 | TRUE | 12-2-065 | Building 12 | WASHING | PW | 2026-08-11 | 2026-08-14 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-08-11 | GOLD01 | VB-05 (12) | PQ3-Week2 | WT-26-0130 | TRUE | WATER SYSTEM (B12) | Building 12 | After Chlorine circulation tank | PRW | 2026-08-11 | 2026-08-14 | 0 | 0 | 0 |  |  | 500 | PASSED | FALSE |  | synced
2026-08-11 | GOLD02 | V50-61 (12) | PQ3-Week2 | WT-26-0130 | TRUE | WATER SYSTEM (B12) | Building 12 | After Cartridge filter 5 µm (B12) | PRW | 2026-08-11 | 2026-08-14 | 8 | 3 | 6 |  |  | 500 | PASSED | FALSE |  | synced
2026-08-11 | GOLD03 | V50-11C (12) | PQ3-Week2 | WT-26-0130 | TRUE | WATER SYSTEM (B12) | Building 12 | After RO (Before EDI) (B12) | RO water | 2026-08-11 | 2026-08-14 | 0 | 0 | 0 |  |  | 500 | PASSED | FALSE |  | synced
2026-08-11 | GOLD04 | V50-39 (12) | PQ3-Week2 | WT-26-0130 | TRUE | WATER SYSTEM (B12) | Building 12 | After EDI (B12) | PW | 2026-08-11 | 2026-08-14 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-08-11 | GOLD07 | SV137.01 | PQ3-Week2 | WT-26-0130 | TRUE | WATER SYSTEM (B12) | Building 12 | Return loop (B12) | PW | 2026-08-11 | 2026-08-14 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-08-11 | OLD02 | SV136.16 | PQ3-Week2 | WT-26-0130 | TRUE | 12-2-057 | Building 12 | CIP 2 | PW | 2026-08-11 | 2026-08-14 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-08-11 | OLD03 | SV136.12 | PQ3-Week2 | WT-26-0130 | TRUE | 12-2-036 | Building 12 | CIP 1 | PW | 2026-08-11 | 2026-08-14 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-08-11 | OLD04 | SV136.07 | PQ3-Week2 | WT-26-0130 | TRUE | 12-2-034 | Building 12 | SYRUP PREPARATION | PW | 2026-08-11 | 2026-08-14 | 21 | 12 | 17 | Commu: PW-M-2-26-009 |  | 100 | PASSED | FALSE |  | synced
2026-08-11 | OLD05 | SV136.06 | PQ3-Week2 | WT-26-0130 | TRUE | 12-2-034 | Building 12 | SYRUP PREPARATION | PW | 2026-08-11 | 2026-08-14 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-08-11 | OLD10 | SV136.15 | PQ3-Week2 | WT-26-0130 | TRUE | 12-2-055 | Building 12 | CIP 3 | PW | 2026-08-11 | 2026-08-14 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-08-11 | OLD12 | SV136.03 | PQ3-Week2 | WT-26-0130 | TRUE | 12-2-032 | Building 12 | CAMPHORATED OPIUM TINCTURE | PW | 2026-08-11 | 2026-08-14 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-08-11 | OLD13 | SV136.05 | PQ3-Week2 | WT-26-0130 | TRUE | 12-2-032 | Building 12 | CAMPHORATED OPIUM TINCTURE | PW | 2026-08-11 | 2026-08-14 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-08-11 | OLD14 | SV136.04 | PQ3-Week2 | WT-26-0130 | TRUE | 12-2-030 | Building 12 | OPIUM TINCTURE | PW | 2026-08-11 | 2026-08-14 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-08-11 | OLD15 | DV136.02 | PQ3-Week2 | WT-26-0130 | TRUE | 12-2-028 | Building 12 | ALCOHOL STORAGE | PW | 2026-08-11 | 2026-08-14 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-08-11 | OLD31 | DV136.07 | PQ3-Week2 | WT-26-0130 | TRUE | 12-3-039 | Building 12 | INSTRUMENT 7 | PW | 2026-08-11 | 2026-08-14 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-08-11 | OLD16 | SV136.14 | Speacial | WT-26-0130 | TRUE | 12-2-045 | Building 12 | MFG 4 | PW | 2026-08-11 | 2026-08-14 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-08-11 | OLD01 | DV136.17 | Speacial | WT-26-0130 | TRUE | 12-2-065 | Building 12 | WASHING | PW | 2026-08-11 | 2026-08-14 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-08-11 | GOCL01 | VB-05 (16) | PQ3-Week2 | WT-26-0131 | TRUE | WATER SYSTEM (B16) | Building 16 | After Chlorine circulation tank (B16) | PRW | 2026-08-11 | 2026-08-14 | 12 | 8 | 10 |  |  | 500 | PASSED | FALSE |  | synced
2026-08-11 | GOCL02 | V50-61 (16) | PQ3-Week2 | WT-26-0131 | TRUE | WATER SYSTEM (B16) | Building 16 | After Cartridge filter 5 µm (B16) | PRW | 2026-08-11 | 2026-08-14 | 0 | 0 | 0 |  |  | 500 | PASSED | FALSE |  | synced
2026-08-11 | GOCL03 | V50-11C (16) | PQ3-Week2 | WT-26-0131 | TRUE | WATER SYSTEM (B16) | Building 16 | After RO (Before EDI) (B16) | RO water | 2026-08-11 | 2026-08-14 | 0 | 0 | 0 |  |  | 500 | PASSED | FALSE |  | synced
2026-08-11 | GOCL04 | V50-39 (16) | PQ3-Week2 | WT-26-0131 | TRUE | WATER SYSTEM (B16) | Building 16 | After EDI (B16) | PW | 2026-08-11 | 2026-08-14 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-08-11 | GOCL08 | SV127.01 | PQ3-Week2 | WT-26-0131 | TRUE | WATER SYSTEM (B16) | Building 16 | Return loop (B16) | PW | 2026-08-11 | 2026-08-14 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-08-11 | OCL09 | DV126.10 | PQ3-Week2 | WT-26-0131 | TRUE | 16-3-069 | Building 16 | MFG 2 | PW | 2026-08-11 | 2026-08-14 | 74 | 58 | 66 | Commu: PW-M-2-26-010 |  | 100 | PASSED | FALSE |  | synced
2026-08-11 | OCL10 | DV126.06 | PQ3-Week2 | WT-26-0131 | TRUE | 16-3-069 | Building 16 | MFG 2 | PW | 2026-08-11 | 2026-08-14 | 1 | 1 | 1 |  |  | 100 | PASSED | FALSE |  | synced
2026-08-11 | OCL11 | SV126.10 | PQ3-Week2 | WT-26-0131 | TRUE | 16-3-071 | Building 16 | MFG 3 (1200L) | PW | 2026-08-11 | 2026-08-14 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-08-11 | OCL12 | SV126.09 | PQ3-Week2 | WT-26-0131 | TRUE | 16-3-071 | Building 16 | MFG 3 (5000L) | PW | 2026-08-11 | 2026-08-14 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-08-11 | OCL19 | DV126.07 | PQ3-Week2 | WT-26-0131 | TRUE | 16-3-077 | Building 16 | MFG 6 | PW | 2026-08-11 | 2026-08-14 | 1 | 0 | 1 |  |  | 100 | PASSED | FALSE |  | synced
2026-08-11 | OCL18 | DV126.08 | PQ3-Week2 | WT-26-0131 | TRUE | 16-3-077 | Building 16 | MFG 6 | PW | 2026-08-11 | 2026-08-14 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-08-13 | GOLD07 | SV137.01 | Speacial | WT-26-0132 | TRUE | WATER SYSTEM (B12) | Building 12 | Return loop (B12) | PW | 2026-08-14 | 2026-08-17 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-08-14 | GOLD07 | SV137.01 | Speacial | WT-26-0133 | TRUE | WATER SYSTEM (B12) | Building 12 | Return loop (B12) | PW | 2026-08-14 | 2026-08-17 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-08-14 | OLD06 | SV136.09 | Speacial | WT-26-0133 | TRUE | 12-2-039 | Building 12 | MFG 1 | PW | 2026-08-14 | 2026-08-17 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-08-14 | OLD01 | DV136.17 | Speacial | WT-26-0133 | TRUE | 12-2-065 | Building 12 | WASHING | PW | 2026-08-14 | 2026-08-17 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-08-14 | GOSD01 | VB-05(10) | PQ3-Week2 | WT-26-0134 | TRUE | WATER SYSTEM (B10) | Building 10 | After Chlorine circulation tank (B10) | PRW | 2026-08-14 | 2026-08-17 | 0 | 0 | 0 |  |  | 500 | PASSED | FALSE |  | synced
2026-08-14 | GOSD03 | V50-61(10) | PQ3-Week2 | WT-26-0134 | TRUE | WATER SYSTEM (B10) | Building 10 | After Cartridge filter 5 µm (B10) | PRW | 2026-08-14 | 2026-08-17 | 0 | 0 | 0 |  |  | 500 | PASSED | FALSE |  | synced
2026-08-14 | GOSD04 | V50-11C(10) | PQ3-Week2 | WT-26-0134 | TRUE | WATER SYSTEM (B10) | Building 10 | After RO (Before EDI) (B10) | RO water | 2026-08-14 | 2026-08-17 | 0 | 0 | 0 |  |  | 500 | PASSED | FALSE |  | synced
2026-08-14 | GOSD05 | V50-39(10) | PQ3-Week2 | WT-26-0134 | TRUE | WATER SYSTEM (B10) | Building 10 | After EDI (B10) | PW | 2026-08-14 | 2026-08-17 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-08-14 | GOSD08 | SV117.01 | PQ3-Week2 | WT-26-0134 | TRUE | WATER SYSTEM (B10) | Building 10 | Return loop (B10) | PW | 2026-08-14 | 2026-08-17 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-08-14 | OSD22 | SV116.05 | PQ3-Week2 | WT-26-0134 | TRUE | 10-3-062 | Building 10 | COATING ROOM-3 | PW | 2026-08-14 | 2026-08-17 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-08-14 | OSD23 | SV116.04 | PQ3-Week2 | WT-26-0134 | TRUE | 10-3-061 | Building 10 | COATING ROOM-2 | PW | 2026-08-14 | 2026-08-17 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-08-14 | OSD24 | DV116.09 | PQ3-Week2 | WT-26-0134 | TRUE | 10-3-060 | Building 10 | COATING SOLUTION PREP.-2 | PW | 2026-08-14 | 2026-08-17 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-08-14 | OSD25 | DV116.08 | PQ3-Week2 | WT-26-0134 | TRUE | 10-3-059 | Building 10 | COATING SOLUTION PREP.-1 | PW | 2026-08-14 | 2026-08-17 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-08-14 | OSD26 | SV116.03 | PQ3-Week2 | WT-26-0134 | TRUE | 10-3-058 | Building 10 | COATING ROOM-1 | PW | 2026-08-14 | 2026-08-17 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-08-14 | OSD29 | SV116.08 | PQ3-Week2 | WT-26-0134 | TRUE | 10-3-067 | Building 10 | COATING ROOM-6 | PW | 2026-08-14 | 2026-08-17 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-08-14 | OSD30 | DV116.11 | PQ3-Week2 | WT-26-0134 | TRUE | 10-3-066 | Building 10 | COATING SOLUTION PREP.-4 | PW | 2026-08-14 | 2026-08-17 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-08-14 | OSD31 | DV116.10 | PQ3-Week2 | WT-26-0134 | TRUE | 10-3-065 | Building 10 | COATING SOLUTION PREP.-3 | PW | 2026-08-14 | 2026-08-17 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-08-14 | OSD32 | SV116.07 | PQ3-Week2 | WT-26-0134 | TRUE | 10-3-064 | Building 10 | COATING ROOM-5 | PW | 2026-08-14 | 2026-08-17 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-08-14 | OSD33 | SV116.06 | PQ3-Week2 | WT-26-0134 | TRUE | 10-3-063 | Building 10 | COATING ROOM-4 | PW | 2026-08-14 | 2026-08-17 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-08-14 | OSD36 | DV116.03 | PQ3-Week2 | WT-26-0134 | TRUE | 10-2-034 | Building 10 | SAMPLE PREPARATION | PW | 2026-08-14 | 2026-08-17 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-08-14 | OSD37 | DV116.06 | PQ3-Week2 | WT-26-0134 | TRUE | 10-2-034 | Building 10 | SAMPLE PREPARATION | PW | 2026-08-14 | 2026-08-17 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-08-14 | OSD38 | DV116.07 | PQ3-Week2 | WT-26-0134 | TRUE | 10-2-032 | Building 10 | GLASS-WARE WASHING | PW | 2026-08-14 | 2026-08-17 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-08-14 | OSD39 | DV116.05 | PQ3-Week2 | WT-26-0134 | TRUE | 10-2-032 | Building 10 | GLASS-WARE WASHING | PW | 2026-08-14 | 2026-08-17 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-08-14 | OSD40 | DV116.04 | PQ3-Week2 | WT-26-0134 | TRUE | 10-2-037 | Building 10 | SKID FOR BIN WASHING-1 | PW | 2026-08-14 | 2026-08-17 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-08-14 | B11 | #N/A | PQ3-Week2 | WT-26-0135 | TRUE | #N/A | Building 11 | #N/A | #N/A | 2026-08-14 | 2026-08-17 | 0 | 0 | 0 |  |  | #N/A | NA | FALSE |  | synced
2026-08-18 | GOLD05 | SV133.01 | PQ3-Week3 | WT-26-0136 | TRUE | WATER SYSTEM (B12) | Building 12 | After Storage tank (B12) | PW | 2026-08-18 | 2026-08-21 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-08-18 | GOLD06 | SV135.02 | PQ3-Week3 | WT-26-0136 | TRUE | WATER SYSTEM (B12) | Building 12 | After UV (B12) | PW | 2026-08-18 | 2026-08-21 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-08-18 | GOLD07 | SV137.01 | PQ3-Week3 | WT-26-0136 | TRUE | WATER SYSTEM (B12) | Building 12 | Return loop (B12) | PW | 2026-08-18 | 2026-08-21 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-08-18 | OLD01 | DV136.17 | PQ3-Week3 | WT-26-0136 | TRUE | 12-2-065 | Building 12 | WASHING | PW | 2026-08-18 | 2026-08-21 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-08-18 | OLD02 | SV136.16 | PQ3-Week3 | WT-26-0136 | TRUE | 12-2-057 | Building 12 | CIP 2 | PW | 2026-08-18 | 2026-08-21 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-08-18 | OLD10 | SV136.15 | PQ3-Week3 | WT-26-0136 | TRUE | 12-2-055 | Building 12 | CIP 3 | PW | 2026-08-18 | 2026-08-21 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-08-18 | OLD17 | DV136.03 | PQ3-Week3 | WT-26-0136 | TRUE | 12-2-053 | Building 12 | IPQC | PW | 2026-08-18 | 2026-08-21 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-08-18 | OLD19 | DV136.01 | PQ3-Week3 | WT-26-0136 | TRUE | 12-1-035 | Building 12 | SUGAR TRANSFERRING | PW | 2026-08-18 | 2026-08-21 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-08-18 | OLD20 | DV136.16 | PQ3-Week3 | WT-26-0136 | TRUE | 12-1-064 | Building 12 | WASHING | PW | 2026-08-18 | 2026-08-21 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-08-18 | OLD34 | DV136.04 | PQ3-Week3 | WT-26-0136 | TRUE | 12-2-077 | Building 12 | WATER SYSTEM ROOM | PW | 2026-08-18 | 2026-08-21 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-08-18 | GOCL05 | SV123.01 | PQ3-Week3 | WT-26-0137 | TRUE | WATER SYSTEM (B16) | Building 16 | After Storage tank (B16) | PW | 2026-08-18 | 2026-08-21 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-08-18 | GOCL07 | SV125.02 | PQ3-Week3 | WT-26-0137 | TRUE | WATER SYSTEM (B16) | Building 16 | After UV (B16) | PW | 2026-08-18 | 2026-08-21 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-08-18 | GOCL08 | SV127.01 | PQ3-Week3 | WT-26-0137 | TRUE | WATER SYSTEM (B16) | Building 16 | Return loop (B16) | PW | 2026-08-18 | 2026-08-21 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-08-18 | OCL06 | SV126.06 | PQ3-Week3 | WT-26-0137 | TRUE | 16-3-067 | Building 16 | MFG 1 | PW | 2026-08-18 | 2026-08-21 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-08-18 | OCL07 | SV126.21 | PQ3-Week3 | WT-26-0137 | TRUE | 16-3-090 | Building 16 | CIP 1 (EQUIPMENT REQUIREMENT) | PW | 2026-08-18 | 2026-08-21 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-08-18 | OCL08 | DV126.09 | PQ3-Week3 | WT-26-0137 | TRUE | 16-3-090 | Building 16 | CIP 1 (ZINK WASHING) | PW | 2026-08-18 | 2026-08-21 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-08-18 | OCL16 | SV126.18 | PQ3-Week3 | WT-26-0137 | TRUE | 16-3-085 | Building 16 | CIP 3 (EQUIPMENT REQUIREMENT) | PW | 2026-08-18 | 2026-08-21 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-08-18 | OCL20 | SV126.05 | PQ3-Week3 | WT-26-0137 | TRUE | 16-3-049 | Building 16 | LINEN WASHING | PW | 2026-08-18 | 2026-08-21 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-08-18 | OCL24 | DV126.04 | PQ3-Week3 | WT-26-0137 | TRUE | 16-2-010 | Building 16 | WATER SYSTEM (PW) | PW | 2026-08-18 | 2026-08-21 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-08-21 | GOSD06 | SV113.01 | PQ3-Week3 | WT-26-0138 | TRUE | WATER SYSTEM (B10) | Building 10 | After Storage tank (B10) | PW | 2026-08-21 | 2026-08-24 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-08-21 | GOSD07 | SV115.02 | PQ3-Week3 | WT-26-0138 | TRUE | WATER SYSTEM (B10) | Building 10 | After UV (B10) | PW | 2026-08-21 | 2026-08-24 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-08-21 | GOSD08 | SV117.01 | PQ3-Week3 | WT-26-0138 | TRUE | WATER SYSTEM (B10) | Building 10 | Return loop (B10) | PW | 2026-08-21 | 2026-08-24 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-08-21 | OSD13 | DV116.25 | PQ3-Week3 | WT-26-0138 | TRUE | 10-3-171 | Building 10 | TOOL WASHING-P | PW | 2026-08-21 | 2026-08-24 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-08-21 | OSD14 | DV116.24 | PQ3-Week3 | WT-26-0138 | TRUE | 10-3-163 | Building 10 | WET GRANULATION 1-P | PW | 2026-08-21 | 2026-08-24 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-08-21 | OSD15 | DV116.23 | PQ3-Week3 | WT-26-0138 | TRUE | 10-3-159 | Building 10 | BINDER PREPARATION-P | PW | 2026-08-21 | 2026-08-24 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-08-21 | OSD16 | DV116.21 | PQ3-Week3 | WT-26-0138 | TRUE | 10-3-152 | Building 10 | WASHING-P | PW | 2026-08-21 | 2026-08-24 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-08-21 | OSD17 | DV116.22 | PQ3-Week3 | WT-26-0138 | TRUE | 10-3-152 | Building 10 | WASHING-P | PW | 2026-08-21 | 2026-08-24 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-08-21 | OSD18 | SV116.13 | PQ3-Week3 | WT-26-0138 | TRUE | 10-3-152 | Building 10 | WASHING-P | PW | 2026-08-21 | 2026-08-24 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-08-21 | OSD19 | DV116.20 | PQ3-Week3 | WT-26-0138 | TRUE | 10-3-149 | Building 10 | IPQC-1-P | PW | 2026-08-21 | 2026-08-24 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-08-21 | OSD20 | DV116.19 | PQ3-Week3 | WT-26-0138 | TRUE | 10-3-143 | Building 10 | COATING SOLUTION PREP.-P | PW | 2026-08-21 | 2026-08-24 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-08-21 | OSD21 | SV116.12 | PQ3-Week3 | WT-26-0138 | TRUE | 10-3-144 | Building 10 | COATING-P | PW | 2026-08-21 | 2026-08-24 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-08-21 | OSD41 | DV116.02 | PQ3-Week3 | WT-26-0138 | TRUE | 10-1-115 | Building 10 | WASHING | PW | 2026-08-21 | 2026-08-24 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-08-21 | OSD42 | DV116.01 | PQ3-Week3 | WT-26-0138 | TRUE | 10-1-057 | Building 10 | WASHING-P | PW | 2026-08-21 | 2026-08-24 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-08-21 | BU19-14 | SV-14 | PQ3-Week3 | WT-26-0139 | TRUE | PROCESS WATER (B19) | Building 19 | AFTER RO SYSTEM NO.12 SV14 | PRW | 2026-08-21 | 2026-08-24 | 142 | 209 | 176 |  |  | 500 | PASSED | FALSE |  | synced
2026-08-25 | GOLD01 | VB-05 (12) | PQ3-Week4 | WT-26-0140 | TRUE | WATER SYSTEM (B12) | Building 12 | After Chlorine circulation tank | PRW | 2026-08-25 | 2026-08-28 | 221 | 235 | 228 |  |  | 500 | PASSED | FALSE |  | synced
2026-08-25 | GOLD02 | V50-61 (12) | PQ3-Week4 | WT-26-0140 | TRUE | WATER SYSTEM (B12) | Building 12 | After Cartridge filter 5 µm (B12) | PRW | 2026-08-25 | 2026-08-28 | 349 | 332 | 341 |  |  | 500 | PASSED | FALSE |  | synced
2026-08-25 | GOLD03 | V50-11C (12) | PQ3-Week4 | WT-26-0140 | TRUE | WATER SYSTEM (B12) | Building 12 | After RO (Before EDI) (B12) | RO water | 2026-08-25 | 2026-08-28 | 0 | 0 | 0 |  |  | 500 | PASSED | FALSE |  | synced
2026-08-25 | GOLD04 | V50-39 (12) | PQ3-Week4 | WT-26-0140 | TRUE | WATER SYSTEM (B12) | Building 12 | After EDI (B12) | PW | 2026-08-25 | 2026-08-28 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-08-25 | GOLD07 | SV137.01 | PQ3-Week4 | WT-26-0140 | TRUE | WATER SYSTEM (B12) | Building 12 | Return loop (B12) | PW | 2026-08-25 | 2026-08-28 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-08-25 | OLD06 | SV136.09 | PQ3-Week4 | WT-26-0140 | TRUE | 12-2-039 | Building 12 | MFG 1 | PW | 2026-08-25 | 2026-08-28 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-08-25 | OLD07 | SV136.10 | PQ3-Week4 | WT-26-0140 | TRUE | 12-2-041 | Building 12 | MFG 2 | PW | 2026-08-25 | 2026-08-28 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-08-25 | OLD08 | SV136.11 | PQ3-Week4 | WT-26-0140 | TRUE | 12-2-043 | Building 12 | MFG 3 | PW | 2026-08-25 | 2026-08-28 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-08-25 | OLD09 | SV136.13 | PQ3-Week4 | WT-26-0140 | TRUE | 12-2-043 | Building 12 | MFG 3 | PW | 2026-08-25 | 2026-08-28 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-08-25 | OLD11 | SV136.08 | PQ3-Week4 | WT-26-0140 | TRUE | 12-2-043 | Building 12 | MFG 3 | PW | 2026-08-25 | 2026-08-28 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-08-25 | OLD16 | SV136.14 | PQ3-Week4 | WT-26-0140 | TRUE | 12-2-045 | Building 12 | MFG 4 | PW | 2026-08-25 | 2026-08-28 | 3 | 0 | 2 |  |  | 100 | PASSED | FALSE |  | synced
2026-08-25 | OLD18 | SV136.02 | PQ3-Week4 | WT-26-0140 | TRUE | 12-2-024 | Building 12 | LIQUORICE EXTRACT | PW | 2026-08-25 | 2026-08-28 | 8 | 2 | 5 |  |  | 100 | PASSED | FALSE |  | synced
2026-08-25 | OLD32 | DV136.08 | PQ3-Week4 | WT-26-0140 | TRUE | 12-3-042 | Building 12 | SAMPLE PREPARATION | PW | 2026-08-25 | 2026-08-28 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-08-25 | OLD33 | DV136.09 | PQ3-Week4 | WT-26-0140 | TRUE | 12-3-042 | Building 12 | SAMPLE PREPARATION | PW | 2026-08-25 | 2026-08-28 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-08-25 | GOCL01 | VB-05 (16) | PQ3-Week4 | WT-26-0141 | TRUE | WATER SYSTEM (B16) | Building 16 | After Chlorine circulation tank (B16) | PRW | 2026-08-25 | 2026-08-28 | 9 | 1 | 5 |  |  | 500 | PASSED | FALSE |  | synced
2026-08-25 | GOCL02 | V50-61 (16) | PQ3-Week4 | WT-26-0141 | TRUE | WATER SYSTEM (B16) | Building 16 | After Cartridge filter 5 µm (B16) | PRW | 2026-08-25 | 2026-08-28 | 49 | 52 | 51 |  |  | 500 | PASSED | FALSE |  | synced
2026-08-25 | GOCL03 | V50-11C (16) | PQ3-Week4 | WT-26-0141 | TRUE | WATER SYSTEM (B16) | Building 16 | After RO (Before EDI) (B16) | RO water | 2026-08-25 | 2026-08-28 | 0 | 0 | 0 |  |  | 500 | PASSED | FALSE |  | synced
2026-08-25 | GOCL04 | V50-39 (16) | PQ3-Week4 | WT-26-0141 | TRUE | WATER SYSTEM (B16) | Building 16 | After EDI (B16) | PW | 2026-08-25 | 2026-08-28 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-08-25 | GOCL08 | SV127.01 | PQ3-Week4 | WT-26-0141 | TRUE | WATER SYSTEM (B16) | Building 16 | Return loop (B16) | PW | 2026-08-25 | 2026-08-28 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-08-25 | OCL13 | SV126.19 | PQ3-Week4 | WT-26-0141 | TRUE | 16-3-087 | Building 16 | CIP 2 (EQUIPMENT REQUIREMENT) | PW | 2026-08-25 | 2026-08-28 | 23 | 33 | 28 | Commu: PW-M-2-26-011 |  | 100 | PASSED | FALSE |  | synced
2026-08-25 | OCL14 | DV126.11 | PQ3-Week4 | WT-26-0141 | TRUE | 16-3-073 | Building 16 | MFG 4 (5000L) | PW | 2026-08-25 | 2026-08-28 | 1 | 0 | 1 |  |  | 100 | PASSED | FALSE |  | synced
2026-08-25 | OCL15 | SV126.14 | PQ3-Week4 | WT-26-0141 | TRUE | 16-3-073 | Building 16 | MFG 4 (400L) | PW | 2026-08-25 | 2026-08-28 | 9 | 8 | 9 | Commu: PW-M-2-26-012 |  | 100 | PASSED | FALSE |  | synced
2026-08-25 | OCL17 | SV126.15 | PQ3-Week4 | WT-26-0141 | TRUE | 16-3-075 | Building 16 | MFG 5 PROCESS (2000L) | PW | 2026-08-25 | 2026-08-28 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-08-25 | OCL21 | DV126.05 | PQ3-Week4 | WT-26-0141 | TRUE | 16-3-054 | Building 16 | WASHING | PW | 2026-08-25 | 2026-08-28 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-08-25 | OCL23 | SV126.04 | PQ3-Week4 | WT-26-0141 | TRUE | 16-2-010 | Building 16 | WATER SYSTEM (PSG) | PW | 2026-08-25 | 2026-08-28 | 4 | 0 | 2 |  |  | 100 | PASSED | FALSE |  | synced
2026-08-28 | GOSD01 | VB-05(10) | PQ3-Week4 | WT-26-0142 | TRUE | WATER SYSTEM (B10) | Building 10 | After Chlorine circulation tank (B10) | PRW | 2026-08-28 | 2026-08-31 | 0 | 0 | 0 |  |  | 500 | PASSED | FALSE |  | synced
2026-08-28 | GOSD03 | V50-61(10) | PQ3-Week4 | WT-26-0142 | TRUE | WATER SYSTEM (B10) | Building 10 | After Cartridge filter 5 µm (B10) | PRW | 2026-08-28 | 2026-08-31 | 34 | 34 | 34 |  |  | 500 | PASSED | FALSE |  | synced
2026-08-28 | GOSD04 | V50-11C(10) | PQ3-Week4 | WT-26-0142 | TRUE | WATER SYSTEM (B10) | Building 10 | After RO (Before EDI) (B10) | RO water | 2026-08-28 | 2026-08-31 | 0 | 0 | 0 |  |  | 500 | PASSED | FALSE |  | synced
2026-08-28 | GOSD05 | V50-39(10) | PQ3-Week4 | WT-26-0142 | TRUE | WATER SYSTEM (B10) | Building 10 | After EDI (B10) | PW | 2026-08-28 | 2026-08-31 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-08-28 | GOSD08 | SV117.01 | PQ3-Week4 | WT-26-0142 | TRUE | WATER SYSTEM (B10) | Building 10 | Return loop (B10) | PW | 2026-08-28 | 2026-08-31 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-08-28 | OSD01 | SV116.15 | PQ3-Week4 | WT-26-0142 | TRUE | 10-4-012 | Building 10 | CIP SKID-1 FOR BIN WASHING-1 | PW | 2026-08-28 | 2026-08-31 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-08-28 | OSD02 | SV116.16 | PQ3-Week4 | WT-26-0142 | TRUE | 10-4-012 | Building 10 | WIP SKID-3 FOR GRANULATION POTENT | PW | 2026-08-28 | 2026-08-31 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-08-28 | OSD03 | SV116.17 | PQ3-Week4 | WT-26-0142 | TRUE | 10-4-012 | Building 10 | CIP SKID-2 FOR BIN WASHING-1 | PW | 2026-08-28 | 2026-08-31 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-08-28 | OSD04 | SV116.18 | PQ3-Week4 | WT-26-0142 | TRUE | 10-4-012 | Building 10 | WIP SKID-1 FOR GRANULATION NON POTENT | PW | 2026-08-28 | 2026-08-31 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-08-28 | OSD05 | SV116.19 | PQ3-Week4 | WT-26-0142 | TRUE | 10-4-012 | Building 10 | WIP SKID-2 FOR GRANULATION NON POTENT | PW | 2026-08-28 | 2026-08-31 | 1 | 4 | 3 |  |  | 100 | PASSED | FALSE |  | synced
2026-08-28 | OSD34 | SV116.02 | PQ3-Week4 | WT-26-0142 | TRUE | 10-2-037 | Building 10 | SKID FOR BIN WASHING-2 | PW | 2026-08-28 | 2026-08-31 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-08-28 | OSD35 | SV116.01 | PQ3-Week4 | WT-26-0142 | TRUE | 10-2-021 | Building 10 | INSTRUMENT-1 | PW | 2026-08-28 | 2026-08-31 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-08-28 | OSD43 | DV116.26 | PQ3-Week4 | WT-26-0142 | TRUE | 10-4-015 | Building 10 | WATER SYSTEM ROOM | PW | 2026-08-28 | 2026-08-31 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-09-01 | GOLD05 | SV133.01 | PQ3-Week1 | WT-26-0143 | TRUE | WATER SYSTEM (B12) | Building 12 | After Storage tank (B12) | PW | 2026-09-01 | 2026-09-05 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-09-01 | GOLD06 | SV135.02 | PQ3-Week1 | WT-26-0143 | TRUE | WATER SYSTEM (B12) | Building 12 | After UV (B12) | PW | 2026-09-01 | 2026-09-05 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-09-01 | GOLD07 | SV137.01 | PQ3-Week1 | WT-26-0143 | TRUE | WATER SYSTEM (B12) | Building 12 | Return loop (B12) | PW | 2026-09-01 | 2026-09-05 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-09-01 | OLD21 | DV136.15 | PQ3-Week1 | WT-26-0143 | TRUE | 12-3-078 | Building 12 | GLASSWARE WASHING 2 | PW | 2026-09-01 | 2026-09-05 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-09-01 | OLD22 | DV136.13 | PQ3-Week1 | WT-26-0143 | TRUE | 12-3-057 | Building 12 | STERILIZATION | PW | 2026-09-01 | 2026-09-05 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-09-01 | OLD23 | SV136.18 | PQ3-Week1 | WT-26-0143 | TRUE | 12-3-059 | Building 12 | AUTOCLAVE | PW | 2026-09-01 | 2026-09-05 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-09-01 | OLD24 | DV136.11 | PQ3-Week1 | WT-26-0143 | TRUE | 12-3-059 | Building 12 | AUTOCLAVE | PW | 2026-09-01 | 2026-09-05 | 4 | 3 | 4 |  |  | 100 | PASSED | FALSE |  | synced
2026-09-01 | OLD25 | DV136.12 | PQ3-Week1 | WT-26-0143 | TRUE | 12-3-056 | Building 12 | MEDIA PREPARATION | PW | 2026-09-01 | 2026-09-05 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-09-01 | OLD26 | DV136.10 | PQ3-Week1 | WT-26-0143 | TRUE | 12-3-056 | Building 12 | MEDIA PREPARATION | PW | 2026-09-01 | 2026-09-05 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-09-01 | OLD27 | DV136.14 | PQ3-Week1 | WT-26-0143 | TRUE | 12-3-074 | Building 12 | DECONTAMINATION | PW | 2026-09-01 | 2026-09-05 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-09-01 | OLD28 | DV136.18 | PQ3-Week1 | WT-26-0143 | TRUE | 12-3-037 | Building 12 | GLASSWARE WASHING 1 | PW | 2026-09-01 | 2026-09-05 | 4 | 8 | 6 |  |  | 100 | PASSED | FALSE |  | synced
2026-09-01 | OLD29 | DV136.05 | PQ3-Week1 | WT-26-0143 | TRUE | 12-3-037 | Building 12 | GLASSWARE WASHING 1 | PW | 2026-09-01 | 2026-09-05 | 39 | 29 | 34 | Commu: PW-M-2-26-013 |  | 100 | PASSED | FALSE |  | synced
2026-09-01 | OLD30 | DV136.06 | PQ3-Week1 | WT-26-0143 | TRUE | 12-3-037 | Building 12 | GLASSWARE WASHING 1 | PW | 2026-09-01 | 2026-09-05 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-09-01 | GOCL05 | SV123.01 | PQ3-Week1 | WT-26-0144 | TRUE | WATER SYSTEM (B16) | Building 16 | After Storage tank (B16) | PW | 2026-09-01 | 2026-09-05 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-09-01 | GOCL07 | SV125.02 | PQ3-Week1 | WT-26-0144 | TRUE | WATER SYSTEM (B16) | Building 16 | After UV (B16) | PW | 2026-09-01 | 2026-09-05 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-09-01 | GOCL08 | SV127.01 | PQ3-Week1 | WT-26-0144 | TRUE | WATER SYSTEM (B16) | Building 16 | Return loop (B16) | PW | 2026-09-01 | 2026-09-05 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-09-01 | OCL01 | DV126.02 | PQ3-Week1 | WT-26-0144 | TRUE | 16-1-082 | Building 16 | WASHING | PW | 2026-09-01 | 2026-09-05 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-09-01 | OCL02 | DV126.01 | PQ3-Week1 | WT-26-0144 | TRUE | 16-1-082 | Building 16 | WASHING | PW | 2026-09-01 | 2026-09-05 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-09-01 | OCL03 | SV126.02 | PQ3-Week1 | WT-26-0144 | TRUE | 16-1-098 | Building 16 | CIP/SIP (EQUIPMENT REQUIREMENT – 200L) | PW | 2026-09-01 | 2026-09-05 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-09-01 | OCL04 | DV126.03 | PQ3-Week1 | WT-26-0144 | TRUE | 16-1-098 | Building 16 | CIP/SIP (SINK WASHING) | PW | 2026-09-01 | 2026-09-05 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-09-01 | OCL05 | SV126.01 | PQ3-Week1 | WT-26-0144 | TRUE | 16-1-092 | Building 16 | LINEN WASHING | PW | 2026-09-01 | 2026-09-05 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-09-01 | OCL22 | SV126.03 | PQ3-Week1 | WT-26-0144 | TRUE | 16-2-010 | Building 16 | WATER SYSTEM (WFI) | PW | 2026-09-01 | 2026-09-05 | 0 | 0 | 0 |  |  | 100 | PASSED | FALSE |  | synced
2026-08-04 | BU19-14 | SV-14 | PQ3-Week1 |  | TRUE | PROCESS WATER (B19) | Building 19 | AFTER RO SYSTEM NO.12 SV14 | PRW | 2026-08-05 | [6 empty] | 500 | NOT-PASSED | FALSE
2026-08-04 | GOSD06 | SV113.01 | PQ3-Week1 |  | TRUE | WATER SYSTEM (B10) | Building 10 | After Storage tank (B10) | PW | 2026-08-05 | [6 empty] | 100 | NOT-PASSED | FALSE
2026-08-04 | GOSD07 | SV115.02 | PQ3-Week1 |  | TRUE | WATER SYSTEM (B10) | Building 10 | After UV (B10) | PW | 2026-08-05 | [6 empty] | 100 | NOT-PASSED | FALSE
2026-08-04 | GOSD08 | SV117.01 | PQ3-Week1 |  | TRUE | WATER SYSTEM (B10) | Building 10 | Return loop (B10) | PW | 2026-08-05 | [6 empty] | 100 | NOT-PASSED | FALSE
2026-08-04 | OSD06 | DV116.18 | PQ3-Week1 |  | TRUE | 10-3-111 | Building 10 | WET GRANULATION-5 | PW | 2026-08-05 | [6 empty] | 100 | NOT-PASSED | FALSE
2026-08-04 | OSD07 | DV116.16 | PQ3-Week1 |  | TRUE | 10-3-107 | Building 10 | WET GRANULATION-2 | PW | 2026-08-05 | [6 empty] | 100 | NOT-PASSED | FALSE
2026-08-04 | OSD08 | SV116.11 | PQ3-Week1 |  | TRUE | 10-3-107 | Building 10 | WET GRANULATION-2 | PW | 2026-08-05 | [6 empty] | 100 | NOT-PASSED | FALSE
2026-08-04 | OSD09 | DV116.14 | PQ3-Week1 |  | TRUE | 10-3-086 | Building 10 | TOOL WASHING | PW | 2026-08-05 | [6 empty] | 100 | NOT-PASSED | FALSE
2026-08-04 | OSD10 | SV116.09 | PQ3-Week1 |  | TRUE | 10-3-078 | Building 10 | WASHING | PW | 2026-08-05 | [6 empty] | 100 | NOT-PASSED | FALSE
2026-08-04 | OSD11 | DV116.13 | PQ3-Week1 |  | TRUE | 10-3-078 | Building 10 | WASHING | PW | 2026-08-05 | [6 empty] | 100 | NOT-PASSED | FALSE
2026-08-04 | OSD12 | DV116.12 | PQ3-Week1 |  | TRUE | 10-3-078 | Building 10 | WASHING | PW | 2026-08-05 | [6 empty] | 100 | NOT-PASSED | FALSE
2026-08-04 | OSD27 | DV116.17 | PQ3-Week1 |  | TRUE | 10-3-117 | Building 10 | IPQC-2 | PW | 2026-08-05 | [6 empty] | 100 | NOT-PASSED | FALSE
2026-08-04 | OSD28 | DV116.15 | PQ3-Week1 |  | TRUE | 10-3-104 | Building 10 | BINDER PREPARATION | PW | 2026-08-05 | [6 empty] | 100 | NOT-PASSED | FALSE
2026-09-08 | GOLD01 | VB-05 (12) | PQ3-Week2 |  | FALSE | WATER SYSTEM (B12) | Building 12 | After Chlorine circulation tank | PRW | 2026-09-08 | [6 empty] | 500 | NOT-PASSED | FALSE
2026-09-08 | GOLD02 | V50-61 (12) | PQ3-Week2 |  | FALSE | WATER SYSTEM (B12) | Building 12 | After Cartridge filter 5 µm (B12) | PRW | 2026-09-08 | [6 empty] | 500 | NOT-PASSED | FALSE
2026-09-08 | GOLD03 | V50-11C (12) | PQ3-Week2 |  | FALSE | WATER SYSTEM (B12) | Building 12 | After RO (Before EDI) (B12) | RO water | 2026-09-08 | [6 empty] | 500 | NOT-PASSED | FALSE
2026-09-08 | GOLD04 | V50-39 (12) | PQ3-Week2 |  | FALSE | WATER SYSTEM (B12) | Building 12 | After EDI (B12) | PW | 2026-09-08 | [6 empty] | 100 | NOT-PASSED | FALSE
2026-09-08 | GOLD07 | SV137.01 | PQ3-Week2 |  | FALSE | WATER SYSTEM (B12) | Building 12 | Return loop (B12) | PW | 2026-09-08 | [6 empty] | 100 | NOT-PASSED | FALSE
2026-09-08 | OLD03 | SV136.12 | PQ3-Week2 |  | FALSE | 12-2-036 | Building 12 | CIP 1 | PW | 2026-09-08 | [6 empty] | 100 | NOT-PASSED | FALSE
2026-09-08 | OLD04 | SV136.07 | PQ3-Week2 |  | FALSE | 12-2-034 | Building 12 | SYRUP PREPARATION | PW | 2026-09-08 | [6 empty] | 100 | NOT-PASSED | FALSE
2026-09-08 | OLD05 | SV136.06 | PQ3-Week2 |  | FALSE | 12-2-034 | Building 12 | SYRUP PREPARATION | PW | 2026-09-08 | [6 empty] | 100 | NOT-PASSED | FALSE
2026-09-08 | OLD12 | SV136.03 | PQ3-Week2 |  | FALSE | 12-2-032 | Building 12 | CAMPHORATED OPIUM TINCTURE | PW | 2026-09-08 | [6 empty] | 100 | NOT-PASSED | FALSE
2026-09-08 | OLD13 | SV136.05 | PQ3-Week2 |  | FALSE | 12-2-032 | Building 12 | CAMPHORATED OPIUM TINCTURE | PW | 2026-09-08 | [6 empty] | 100 | NOT-PASSED | FALSE
2026-09-08 | OLD14 | SV136.04 | PQ3-Week2 |  | FALSE | 12-2-030 | Building 12 | OPIUM TINCTURE | PW | 2026-09-08 | [6 empty] | 100 | NOT-PASSED | FALSE
2026-09-08 | OLD15 | DV136.02 | PQ3-Week2 |  | FALSE | 12-2-028 | Building 12 | ALCOHOL STORAGE | PW | 2026-09-08 | [6 empty] | 100 | NOT-PASSED | FALSE
2026-09-08 | OLD31 | DV136.07 | PQ3-Week2 |  | FALSE | 12-3-039 | Building 12 | INSTRUMENT 7 | PW | 2026-09-08 | [6 empty] | 100 | NOT-PASSED | FALSE
2026-09-08 | GOCL01 | VB-05 (16) | PQ3-Week2 |  | FALSE | WATER SYSTEM (B16) | Building 16 | After Chlorine circulation tank (B16) | PRW | 2026-09-08 | [6 empty] | 500 | NOT-PASSED | FALSE
2026-09-08 | GOCL02 | V50-61 (16) | PQ3-Week2 |  | FALSE | WATER SYSTEM (B16) | Building 16 | After Cartridge filter 5 µm (B16) | PRW | 2026-09-08 | [6 empty] | 500 | NOT-PASSED | FALSE
2026-09-08 | GOCL03 | V50-11C (16) | PQ3-Week2 |  | FALSE | WATER SYSTEM (B16) | Building 16 | After RO (Before EDI) (B16) | RO water | 2026-09-08 | [6 empty] | 500 | NOT-PASSED | FALSE
2026-09-08 | GOCL04 | V50-39 (16) | PQ3-Week2 |  | FALSE | WATER SYSTEM (B16) | Building 16 | After EDI (B16) | PW | 2026-09-08 | [6 empty] | 100 | NOT-PASSED | FALSE
2026-09-08 | GOCL08 | SV127.01 | PQ3-Week2 |  | FALSE | WATER SYSTEM (B16) | Building 16 | Return loop (B16) | PW | 2026-09-08 | [6 empty] | 100 | NOT-PASSED | FALSE
2026-09-08 | OCL09 | DV126.10 | PQ3-Week2 |  | FALSE | 16-3-069 | Building 16 | MFG 2 | PW | 2026-09-08 | [6 empty] | 100 | NOT-PASSED | FALSE
2026-09-08 | OCL10 | DV126.06 | PQ3-Week2 |  | FALSE | 16-3-069 | Building 16 | MFG 2 | PW | 2026-09-08 | [6 empty] | 100 | NOT-PASSED | FALSE
2026-09-08 | OCL11 | SV126.10 | PQ3-Week2 |  | FALSE | 16-3-071 | Building 16 | MFG 3 (1200L) | PW | 2026-09-08 | [6 empty] | 100 | NOT-PASSED | FALSE
2026-09-08 | OCL12 | SV126.09 | PQ3-Week2 |  | FALSE | 16-3-071 | Building 16 | MFG 3 (5000L) | PW | 2026-09-08 | [6 empty] | 100 | NOT-PASSED | FALSE
Formulas:
performedDate = [samplingDate]+1

## wfi-pus
samplingDate | samplingPoint | samplingTag | recordStatus | worksheet No. | worksheetCreate | noLocation | building | location | waterType | performedDate | determinedDate | result1 | resultAvg | qualityEvent | comment | criteria | statusResult | Exclude | status | syncStatus
2026-05-28 | WFI06 | SV216.05 | PQ3-Day4 | WP-26-0080 | TRUE | 16-1-110 | Building 16 | DISINFECTANT PREPARATION | WFI | 2026-05-30 | 2026-06-02 | 0 | 0 |  |  |  | PASSED | FALSE |  | synced
2026-05-28 | WFI09 | SV216.10 | PQ3-Day4 | WP-26-0080 | TRUE | 16-1-105 | Building 16 | WASHING/TUNNEL-01 | WFI | 2026-05-30 | 2026-06-02 | 0 | 0 |  |  |  | PASSED | FALSE |  | synced
2026-05-29 | WFI10 | POU HE216.04 | PQ3-Day5 | WP-26-0081 | TRUE | 16-1-114 | Building 16 | COMPOUNDING-02 | WFI | 2026-05-30 | 2026-06-02 | 0 | 0 |  |  |  | PASSED | FALSE |  | synced
2026-05-29 | WFI11 | POU HE216.05 | PQ3-Day5 | WP-26-0081 | TRUE | 16-1-114 | Building 16 | COMPOUNDING-02 | WFI | 2026-05-30 | 2026-06-02 | 0 | 0 |  |  |  | PASSED | FALSE |  | synced
2026-06-02 | GWFI01 | V12-4 | PQ3-Day1 | WP-26-0082 | TRUE | 16-2-010 | Building 16 | AFTER WFI GENERATOR | WFI | 2026-06-03 | 2026-06-06 | 0 | 0 |  |  |  | PASSED | FALSE |  | synced
2026-06-02 | GWFI02 | SV213.01 | PQ3-Day1 | WP-26-0082 | TRUE | 16-2-010 | Building 16 | AFTER STORAGE TANK | WFI | 2026-06-03 | 2026-06-06 | 0 | 0 |  |  |  | PASSED | FALSE |  | synced
2026-06-02 | GWFI03 | SV217.01 | PQ3-Day1 | WP-26-0082 | TRUE | 16-2-010 | Building 16 | RETURN LOOP | WFI | 2026-06-03 | 2026-06-06 | 0 | 0 |  |  |  | PASSED | FALSE |  | synced
2026-06-02 | WFI03 | SV216.03 | PQ3-Day1 | WP-26-0082 | TRUE | 16-1-096 | Building 16 | WASHING/TUNNEL-02 | WFI | 2026-06-03 | 2026-06-06 | 0 | 0 |  |  |  | PASSED | FALSE |  | synced
2026-06-02 | WFI04 | POU HE216.03 | PQ3-Day1 | WP-26-0082 | TRUE | 16-1-082 | Building 16 | WASHING | WFI | 2026-06-03 | 2026-06-06 | 0 | 0 |  |  |  | PASSED | FALSE |  | synced
2026-06-02 | WFI05 | SV216.06 | PQ3-Day1 | WP-26-0082 | TRUE | 16-1-082 | Building 16 | WASHING | WFI | 2026-06-03 | 2026-06-06 | 0 | 0 |  |  |  | PASSED | FALSE |  | synced
2026-06-04 | WFI01 | POU HE216.01 | PQ3-Day2 | WP-26-0083 | TRUE | 16-1-107 | Building 16 | COMPOUNDING-01 | WFI | 2026-06-05 | 2026-06-08 | 0 | 0 |  |  |  | PASSED | FALSE |  | synced
2026-06-04 | WFI02 | POU HE216.02 | PQ3-Day2 | WP-26-0083 | TRUE | 16-1-107 | Building 16 | COMPOUNDING-01 | WFI | 2026-06-05 | 2026-06-08 | 0 | 0 |  |  |  | PASSED | FALSE |  | synced
2026-06-04 | WFI09 | SV216.10 | PQ3-Day2 | WP-26-0083 | TRUE | 16-1-105 | Building 16 | WASHING/TUNNEL-01 | WFI | 2026-06-05 | 2026-06-08 | 0 | 0 |  |  |  | PASSED | FALSE |  | synced
2026-06-05 | WFI06 | SV216.05 | PQ3-Day3 | WP-26-0084 | TRUE | 16-1-110 | Building 16 | DISINFECTANT PREPARATION | WFI | 2026-06-05 | 2026-06-08 | 0 | 0 |  |  |  | PASSED | FALSE |  | synced
2026-06-05 | WFI07 | SV216.02 | PQ3-Day3 | WP-26-0084 | TRUE | 16-1-098 | Building 16 | CIP/SIP | WFI | 2026-06-05 | 2026-06-08 | 0 | 0 |  |  |  | PASSED | FALSE |  | synced
2026-06-05 | WFI08 | SV216.04 | PQ3-Day3 | WP-26-0084 | TRUE | 16-1-098 | Building 16 | CIP/SIP | WFI | 2026-06-05 | 2026-06-08 | 0 | 0 |  |  |  | PASSED | FALSE |  | synced
2026-06-05 | WFI10 | POU HE216.04 | PQ3-Day3 | WP-26-0084 | TRUE | 16-1-114 | Building 16 | COMPOUNDING-02 | WFI | 2026-06-05 | 2026-06-08 | 0 | 0 |  |  |  | PASSED | FALSE |  | synced
2026-06-05 | WFI11 | POU HE216.05 | PQ3-Day3 | WP-26-0084 | TRUE | 16-1-114 | Building 16 | COMPOUNDING-02 | WFI | 2026-06-05 | 2026-06-08 | 0 | 0 |  |  |  | PASSED | FALSE |  | synced
2026-06-08 | GWFI01 | V12-4 | PQ3-Day1 | WP-26-0085 | TRUE | 16-2-010 | Building 16 | AFTER WFI GENERATOR | WFI | 2026-06-09 | 2026-06-12 | 0 | 0 |  |  |  | PASSED | FALSE |  | synced
2026-06-08 | GWFI02 | SV213.01 | PQ3-Day1 | WP-26-0085 | TRUE | 16-2-010 | Building 16 | AFTER STORAGE TANK | WFI | 2026-06-09 | 2026-06-12 | 0 | 0 |  |  |  | PASSED | FALSE |  | synced
2026-06-08 | GWFI03 | SV217.01 | PQ3-Day1 | WP-26-0085 | TRUE | 16-2-010 | Building 16 | RETURN LOOP | WFI | 2026-06-09 | 2026-06-12 | 0 | 0 |  |  |  | PASSED | FALSE |  | synced
2026-06-08 | WFI07 | SV216.02 | PQ3-Day1 | WP-26-0085 | TRUE | 16-1-098 | Building 16 | CIP/SIP | WFI | 2026-06-09 | 2026-06-12 | 0 | 0 |  |  |  | PASSED | FALSE |  | synced
2026-06-08 | WFI08 | SV216.04 | PQ3-Day1 | WP-26-0085 | TRUE | 16-1-098 | Building 16 | CIP/SIP | WFI | 2026-06-09 | 2026-06-12 | 0 | 0 |  |  |  | PASSED | FALSE |  | synced
2026-06-09 | WFI03 | SV216.03 | PQ3-Day2 | WP-26-0086 | TRUE | 16-1-096 | Building 16 | WASHING/TUNNEL-02 | WFI | 2026-06-09 | 2026-06-12 | 0 | 0 |  |  |  | PASSED | FALSE |  | synced
2026-06-09 | WFI04 | POU HE216.03 | PQ3-Day2 | WP-26-0086 | TRUE | 16-1-082 | Building 16 | WASHING | WFI | 2026-06-09 | 2026-06-12 | 0 | 0 |  |  |  | PASSED | FALSE |  | synced
2026-06-09 | WFI05 | SV216.06 | PQ3-Day2 | WP-26-0086 | TRUE | 16-1-082 | Building 16 | WASHING | WFI | 2026-06-09 | 2026-06-12 | 0 | 0 |  |  |  | PASSED | FALSE |  | synced
2026-06-10 | WFI01 | POU HE216.01 | PQ3-Day3 | WP-26-0087 | TRUE | 16-1-107 | Building 16 | COMPOUNDING-01 | WFI | 2026-06-11 | 2026-06-15 | 16 | 16 | IR: 1100003786 |  |  | NOT-PASSED | FALSE |  | synced
2026-06-10 | WFI02 | POU HE216.02 | PQ3-Day3 | WP-26-0087 | TRUE | 16-1-107 | Building 16 | COMPOUNDING-01 | WFI | 2026-06-11 | 2026-06-15 | 0 | 0 |  |  |  | PASSED | FALSE |  | synced
2026-06-11 | WFI06 | SV216.05 | PQ3-Day4 | WP-26-0088 | TRUE | 16-1-110 | Building 16 | DISINFECTANT PREPARATION | WFI | 2026-06-11 | 2026-06-15 | 0 | 0 |  |  |  | PASSED | FALSE |  | synced
2026-06-11 | WFI09 | SV216.10 | PQ3-Day4 | WP-26-0088 | TRUE | 16-1-105 | Building 16 | WASHING/TUNNEL-01 | WFI | 2026-06-11 | 2026-06-15 | 0 | 0 |  |  |  | PASSED | FALSE |  | synced
2026-06-12 | WFI10 | POU HE216.04 | PQ3-Day5 | WP-26-0089 | TRUE | 16-1-114 | Building 16 | COMPOUNDING-02 | WFI | 2026-06-12 | 2026-06-15 | 0 | 0 |  |  |  | PASSED | FALSE |  | synced
2026-06-12 | WFI11 | POU HE216.05 | PQ3-Day5 | WP-26-0089 | TRUE | 16-1-114 | Building 16 | COMPOUNDING-02 | WFI | 2026-06-12 | 2026-06-15 | 0 | 0 |  |  |  | PASSED | FALSE |  | synced
2026-06-15 | GWFI01 | V12-4 | PQ3-Day1 | WP-26-0090 | TRUE | 16-2-010 | Building 16 | AFTER WFI GENERATOR | WFI | 2026-06-16 | 2026-06-19 | 0 | 0 |  |  |  | PASSED | FALSE |  | synced
2026-06-15 | GWFI02 | SV213.01 | PQ3-Day1 | WP-26-0090 | TRUE | 16-2-010 | Building 16 | AFTER STORAGE TANK | WFI | 2026-06-16 | 2026-06-19 | 0 | 0 |  |  |  | PASSED | FALSE |  | synced
2026-06-15 | GWFI03 | SV217.01 | PQ3-Day1 | WP-26-0090 | TRUE | 16-2-010 | Building 16 | RETURN LOOP | WFI | 2026-06-16 | 2026-06-19 | 0 | 0 |  |  |  | PASSED | FALSE |  | synced
2026-06-15 | WFI07 | SV216.02 | PQ3-Day1 | WP-26-0090 | TRUE | 16-1-098 | Building 16 | CIP/SIP | WFI | 2026-06-16 | 2026-06-19 | 0 | 0 |  |  |  | PASSED | FALSE |  | synced
2026-06-15 | WFI08 | SV216.04 | PQ3-Day1 | WP-26-0090 | TRUE | 16-1-098 | Building 16 | CIP/SIP | WFI | 2026-06-16 | 2026-06-19 | 0 | 0 |  |  |  | PASSED | FALSE |  | synced
2026-06-16 | WFI03 | SV216.03 | PQ3-Day2 | WP-26-0091 | TRUE | 16-1-096 | Building 16 | WASHING/TUNNEL-02 | WFI | 2026-06-18 | 2026-06-22 | 0 | 0 |  |  |  | PASSED | FALSE |  | synced
2026-06-16 | WFI04 | POU HE216.03 | PQ3-Day2 | WP-26-0091 | TRUE | 16-1-082 | Building 16 | WASHING | WFI | 2026-06-18 | 2026-06-22 | 0 | 0 |  |  |  | PASSED | FALSE |  | synced
2026-06-16 | WFI05 | SV216.06 | PQ3-Day2 | WP-26-0091 | TRUE | 16-1-082 | Building 16 | WASHING | WFI | 2026-06-18 | 2026-06-22 | 0 | 0 |  |  |  | PASSED | FALSE |  | synced
2026-06-17 | WFI01 | POU HE216.01 | PQ3-Day3 | WP-26-0092 | TRUE | 16-1-107 | Building 16 | COMPOUNDING-01 | WFI | 2026-06-18 | 2026-06-22 | 9 | 9 | COMMU: WFI-M-2-26-001 |  |  | NOT-PASSED | FALSE |  | synced
2026-06-17 | WFI02 | POU HE216.02 | PQ3-Day3 | WP-26-0092 | TRUE | 16-1-107 | Building 16 | COMPOUNDING-01 | WFI | 2026-06-18 | 2026-06-22 | 0 | 0 |  |  |  | PASSED | FALSE |  | synced
2026-06-18 | WFI06 | SV216.05 | PQ3-Day4 | WP-26-0093 | TRUE | 16-1-110 | Building 16 | DISINFECTANT PREPARATION | WFI | 2026-06-20 | 2026-06-23 | 0 | 0 |  |  |  | PASSED | FALSE |  | synced
2026-06-18 | WFI09 | SV216.10 | PQ3-Day4 | WP-26-0093 | TRUE | 16-1-105 | Building 16 | WASHING/TUNNEL-01 | WFI | 2026-06-20 | 2026-06-23 | 0 | 0 |  |  |  | PASSED | FALSE |  | synced
2026-06-19 | WFI10 | POU HE216.04 | PQ3-Day5 | WP-26-0094 | TRUE | 16-1-114 | Building 16 | COMPOUNDING-02 | WFI | 2026-06-20 | 2026-06-23 | 0 | 0 |  |  |  | PASSED | FALSE |  | synced
2026-06-19 | WFI11 | POU HE216.05 | PQ3-Day5 | WP-26-0094 | TRUE | 16-1-114 | Building 16 | COMPOUNDING-02 | WFI | 2026-06-20 | 2026-06-23 | 0 | 0 |  |  |  | PASSED | FALSE |  | synced
2026-06-22 | GWFI01 | V12-4 | PQ3-Day1 | WP-26-0095 | TRUE | 16-2-010 | Building 16 | AFTER WFI GENERATOR | WFI | 2026-06-23 | 2026-06-26 | 0 | 0 |  |  |  | PASSED | FALSE |  | synced
2026-06-22 | GWFI02 | SV213.01 | PQ3-Day1 | WP-26-0095 | TRUE | 16-2-010 | Building 16 | AFTER STORAGE TANK | WFI | 2026-06-23 | 2026-06-26 | 0 | 0 |  |  |  | PASSED | FALSE |  | synced
2026-06-22 | GWFI03 | SV217.01 | PQ3-Day1 | WP-26-0095 | TRUE | 16-2-010 | Building 16 | RETURN LOOP | WFI | 2026-06-23 | 2026-06-26 | 0 | 0 |  |  |  | PASSED | FALSE |  | synced
2026-06-22 | WFI07 | SV216.02 | PQ3-Day1 | WP-26-0095 | TRUE | 16-1-098 | Building 16 | CIP/SIP | WFI | 2026-06-23 | 2026-06-26 | 0 | 0 |  |  |  | PASSED | FALSE |  | synced
2026-06-22 | WFI08 | SV216.04 | PQ3-Day1 | WP-26-0095 | TRUE | 16-1-098 | Building 16 | CIP/SIP | WFI | 2026-06-23 | 2026-06-26 | 0 | 0 |  |  |  | PASSED | FALSE |  | synced
2026-06-23 | WFI03 | SV216.03 | PQ3-Day2 | WP-26-0096 | TRUE | 16-1-096 | Building 16 | WASHING/TUNNEL-02 | WFI | 2026-06-25 | 2026-06-29 | 0 | 0 |  |  |  | PASSED | FALSE |  | synced
2026-06-23 | WFI04 | POU HE216.03 | PQ3-Day2 | WP-26-0096 | TRUE | 16-1-082 | Building 16 | WASHING | WFI | 2026-06-25 | 2026-06-29 | 0 | 0 |  |  |  | PASSED | FALSE |  | synced
2026-06-23 | WFI05 | SV216.06 | PQ3-Day2 | WP-26-0096 | TRUE | 16-1-082 | Building 16 | WASHING | WFI | 2026-06-25 | 2026-06-29 | 0 | 0 |  |  |  | PASSED | FALSE |  | synced
2026-06-24 | WFI01 | POU HE216.01 | PQ3-Day3 | WP-26-0097 | TRUE | 16-1-107 | Building 16 | COMPOUNDING-01 | WFI | 2026-06-25 | 2026-06-29 | 2 | 2 |  |  |  | NOT-PASSED | FALSE |  | synced
2026-06-24 | WFI02 | POU HE216.02 | PQ3-Day3 | WP-26-0097 | TRUE | 16-1-107 | Building 16 | COMPOUNDING-01 | WFI | 2026-06-25 | 2026-06-29 | 83 | 83 | OOS 69-ANF3-016 |  |  | NOT-PASSED | FALSE |  | synced
2026-06-25 | WFI06 | SV216.05 | PQ3-Day4 | WP-26-0098 | TRUE | 16-1-110 | Building 16 | DISINFECTANT PREPARATION | WFI | 2026-06-27 | 2026-06-30 | 0 | 0 |  |  |  | PASSED | FALSE |  | synced
2026-06-25 | WFI09 | SV216.10 | PQ3-Day4 | WP-26-0098 | TRUE | 16-1-105 | Building 16 | WASHING/TUNNEL-01 | WFI | 2026-06-27 | 2026-06-30 | 0 | 0 |  |  |  | PASSED | FALSE |  | synced
2026-06-26 | WFI10 | POU HE216.04 | PQ3-Day5 | WP-26-0099 | TRUE | 16-1-114 | Building 16 | COMPOUNDING-02 | WFI | 2026-06-27 | 2026-06-30 | 0 | 0 |  |  |  | PASSED | FALSE |  | synced
2026-06-26 | WFI11 | POU HE216.05 | PQ3-Day5 | WP-26-0099 | TRUE | 16-1-114 | Building 16 | COMPOUNDING-02 | WFI | 2026-06-27 | 2026-06-30 | 0 | 0 |  |  |  | PASSED | FALSE |  | synced
2026-06-29 | GWFI01 | V12-4 | PQ3-Day1 | WP-26-0100 | TRUE | 16-2-010 | Building 16 | AFTER WFI GENERATOR | WFI | 2026-06-30 | 2026-07-03 | 0 | 0 |  |  |  | PASSED | FALSE |  | synced
2026-06-29 | GWFI02 | SV213.01 | PQ3-Day1 | WP-26-0100 | TRUE | 16-2-010 | Building 16 | AFTER STORAGE TANK | WFI | 2026-06-30 | 2026-07-03 | 0 | 0 |  |  |  | PASSED | FALSE |  | synced
2026-06-29 | GWFI03 | SV217.01 | PQ3-Day1 | WP-26-0100 | TRUE | 16-2-010 | Building 16 | RETURN LOOP | WFI | 2026-06-30 | 2026-07-03 | 0 | 0 |  |  |  | PASSED | FALSE |  | synced
2026-06-29 | WFI07 | SV216.02 | PQ3-Day1 | WP-26-0100 | TRUE | 16-1-098 | Building 16 | CIP/SIP | WFI | 2026-06-30 | 2026-07-03 | 0 | 0 |  |  |  | PASSED | FALSE |  | synced
2026-06-29 | WFI08 | SV216.04 | PQ3-Day1 | WP-26-0100 | TRUE | 16-1-098 | Building 16 | CIP/SIP | WFI | 2026-06-30 | 2026-07-03 | 0 | 0 |  |  |  | PASSED | FALSE |  | synced
2026-06-30 | WFI03 | SV216.03 | PQ3-Day2 | WP-26-0101 | TRUE | 16-1-096 | Building 16 | WASHING/TUNNEL-02 | WFI | 2026-07-02 | 2026-06-06 | 0 | 0 |  |  |  | PASSED | FALSE |  | synced
2026-06-30 | WFI04 | POU HE216.03 | PQ3-Day2 | WP-26-0101 | TRUE | 16-1-082 | Building 16 | WASHING | WFI | 2026-07-02 | 2026-06-06 | 0 | 0 |  |  |  | PASSED | FALSE |  | synced
2026-06-30 | WFI05 | SV216.06 | PQ3-Day2 | WP-26-0101 | TRUE | 16-1-082 | Building 16 | WASHING | WFI | 2026-07-02 | 2026-06-06 | 0 | 0 |  |  |  | PASSED | FALSE |  | synced
2026-07-01 | WFI01 | POU HE216.01 | PQ3-Day3 | WP-26-0102 | TRUE | 16-1-107 | Building 16 | COMPOUNDING-01 | WFI | 2026-07-02 | 2026-06-06 | 17 | 17 | IR: 1100003879 |  |  | NOT-PASSED | FALSE |  | synced
2026-07-01 | WFI02 | POU HE216.02 | PQ3-Day3 | WP-26-0102 | TRUE | 16-1-107 | Building 16 | COMPOUNDING-01 | WFI | 2026-07-02 | 2026-06-06 | 0 | 0 |  |  |  | PASSED | FALSE |  | synced
2026-07-02 | WFI06 | SV216.05 | PQ3-Day4 | WP-26-0103 | TRUE | 16-1-110 | Building 16 | DISINFECTANT PREPARATION | WFI | 2026-07-02 | 2026-06-06 | 0 | 0 |  |  |  | PASSED | FALSE |  | synced
2026-07-02 | WFI09 | SV216.10 | PQ3-Day4 | WP-26-0103 | TRUE | 16-1-105 | Building 16 | WASHING/TUNNEL-01 | WFI | 2026-07-02 | 2026-06-06 | 0 | 0 |  |  |  | PASSED | FALSE |  | synced
2026-07-03 | WFI10 | POU HE216.04 | PQ3-Day5 | WP-26-0104 | TRUE | 16-1-114 | Building 16 | COMPOUNDING-02 | WFI | 2026-07-03 | 2026-06-06 | 0 | 0 |  |  |  | PASSED | FALSE |  | synced
2026-07-03 | WFI11 | POU HE216.05 | PQ3-Day5 | WP-26-0104 | TRUE | 16-1-114 | Building 16 | COMPOUNDING-02 | WFI | 2026-07-03 | 2026-06-06 | 0 | 0 |  |  |  | PASSED | FALSE |  | synced
2026-07-06 | GWFI01 | V12-4 | PQ3-Day1 | WP-26-0105 | TRUE | 16-2-010 | Building 16 | AFTER WFI GENERATOR | WFI | 2026-07-07 | 2026-07-10 | 0 | 0 |  |  |  | PASSED | FALSE |  | synced
2026-07-06 | GWFI02 | SV213.01 | PQ3-Day1 | WP-26-0105 | TRUE | 16-2-010 | Building 16 | AFTER STORAGE TANK | WFI | 2026-07-07 | 2026-07-10 | 0 | 0 |  |  |  | PASSED | FALSE |  | synced
2026-07-06 | GWFI03 | SV217.01 | PQ3-Day1 | WP-26-0105 | TRUE | 16-2-010 | Building 16 | RETURN LOOP | WFI | 2026-07-07 | 2026-07-10 | 0 | 0 |  |  |  | PASSED | FALSE |  | synced
2026-07-06 | WFI07 | SV216.02 | PQ3-Day1 | WP-26-0105 | TRUE | 16-1-098 | Building 16 | CIP/SIP | WFI | 2026-07-07 | 2026-07-10 | 0 | 0 |  |  |  | PASSED | FALSE |  | synced
2026-07-06 | WFI08 | SV216.04 | PQ3-Day1 | WP-26-0105 | TRUE | 16-1-098 | Building 16 | CIP/SIP | WFI | 2026-07-07 | 2026-07-10 | 0 | 0 |  |  |  | PASSED | FALSE |  | synced
2026-07-07 | WFI03 | SV216.03 | PQ3-Day2 | WP-26-0106 | TRUE | 16-1-096 | Building 16 | WASHING/TUNNEL-02 | WFI | 2026-07-07 | 2026-07-10 | 0 | 0 |  |  |  | PASSED | FALSE |  | synced
2026-07-07 | WFI04 | POU HE216.03 | PQ3-Day2 | WP-26-0106 | TRUE | 16-1-082 | Building 16 | WASHING | WFI | 2026-07-07 | 2026-07-10 | 0 | 0 |  |  |  | PASSED | FALSE |  | synced
2026-07-07 | WFI05 | SV216.06 | PQ3-Day2 | WP-26-0106 | TRUE | 16-1-082 | Building 16 | WASHING | WFI | 2026-07-07 | 2026-07-10 | 0 | 0 |  |  |  | PASSED | FALSE |  | synced
2026-07-08 | WFI01 | POU HE216.01 | PQ3-Day3 | WP-26-0107 | TRUE | 16-1-107 | Building 16 | COMPOUNDING-01 | WFI | 2026-07-09 | 2026-07-12 | 0 | 0 |  |  |  | PASSED | FALSE |  | synced
2026-07-08 | WFI02 | POU HE216.02 | PQ3-Day3 | WP-26-0107 | TRUE | 16-1-107 | Building 16 | COMPOUNDING-01 | WFI | 2026-07-09 | 2026-07-12 | 0 | 0 |  |  |  | PASSED | FALSE |  | synced
2026-07-09 | WFI06 | SV216.05 | PQ3-Day4 | WP-26-0108 | TRUE | 16-1-110 | Building 16 | DISINFECTANT PREPARATION | WFI | 2026-07-09 | 2026-07-12 | 0 | 0 |  |  |  | PASSED | FALSE |  | synced
2026-07-09 | WFI09 | SV216.10 | PQ3-Day4 | WP-26-0108 | TRUE | 16-1-105 | Building 16 | WASHING/TUNNEL-01 | WFI | 2026-07-09 | 2026-07-12 | 0 | 0 |  |  |  | PASSED | FALSE |  | synced
2026-07-10 | WFI10 | POU HE216.04 | PQ3-Day5 | WP-26-0109 | TRUE | 16-1-114 | Building 16 | COMPOUNDING-02 | WFI | 2026-07-11 | 2026-07-14 | 0 | 0 |  |  |  | PASSED | FALSE |  | synced
2026-07-10 | WFI11 | POU HE216.05 | PQ3-Day5 | WP-26-0109 | TRUE | 16-1-114 | Building 16 | COMPOUNDING-02 | WFI | 2026-07-11 | 2026-07-14 | 0 | 0 |  |  |  | PASSED | FALSE |  | synced
2026-07-13 | GWFI01 | V12-4 | PQ3-Day1 | WP-26-0110 | TRUE | 16-2-010 | Building 16 | AFTER WFI GENERATOR | WFI | 2026-07-14 | 2026-07-17 | 0 | 0 |  |  |  | PASSED | FALSE |  | synced
2026-07-13 | GWFI02 | SV213.01 | PQ3-Day1 | WP-26-0110 | TRUE | 16-2-010 | Building 16 | AFTER STORAGE TANK | WFI | 2026-07-14 | 2026-07-17 | 0 | 0 |  |  |  | PASSED | FALSE |  | synced
2026-07-13 | GWFI03 | SV217.01 | PQ3-Day1 | WP-26-0110 | TRUE | 16-2-010 | Building 16 | RETURN LOOP | WFI | 2026-07-14 | 2026-07-17 | 0 | 0 |  |  |  | PASSED | FALSE |  | synced
2026-07-13 | WFI07 | SV216.02 | PQ3-Day1 | WP-26-0110 | TRUE | 16-1-098 | Building 16 | CIP/SIP | WFI | 2026-07-14 | 2026-07-17 | 0 | 0 |  |  |  | PASSED | FALSE |  | synced
2026-07-13 | WFI08 | SV216.04 | PQ3-Day1 | WP-26-0110 | TRUE | 16-1-098 | Building 16 | CIP/SIP | WFI | 2026-07-14 | 2026-07-17 | 0 | 0 |  |  |  | PASSED | FALSE |  | synced
2026-07-14 | WFI03 | SV216.03 | PQ3-Day2 | WP-26-0111 | TRUE | 16-1-096 | Building 16 | WASHING/TUNNEL-02 | WFI | 2026-07-16 | 2026-07-19 | 0 | 0 |  |  |  | PASSED | FALSE |  | synced
2026-07-14 | WFI04 | POU HE216.03 | PQ3-Day2 | WP-26-0111 | TRUE | 16-1-082 | Building 16 | WASHING | WFI | 2026-07-16 | 2026-07-19 | 0 | 0 |  |  |  | PASSED | FALSE |  | synced
2026-07-14 | WFI05 | SV216.06 | PQ3-Day2 | WP-26-0111 | TRUE | 16-1-082 | Building 16 | WASHING | WFI | 2026-07-16 | 2026-07-19 | 0 | 0 |  |  |  | PASSED | FALSE |  | synced
2026-07-15 | WFI01 | POU HE216.01 | PQ3-Day3 | WP-26-0112 | TRUE | 16-1-107 | Building 16 | COMPOUNDING-01 | WFI | 2026-07-16 | 2026-07-19 | 0 | 0 |  |  |  | PASSED | FALSE |  | synced
2026-07-15 | WFI02 | POU HE216.02 | PQ3-Day3 | WP-26-0112 | TRUE | 16-1-107 | Building 16 | COMPOUNDING-01 | WFI | 2026-07-16 | 2026-07-19 | 0 | 0 |  |  |  | PASSED | FALSE |  | synced
2026-07-16 | WFI06 | SV216.05 | PQ3-Day4 | WP-26-0113 | TRUE | 16-1-110 | Building 16 | DISINFECTANT PREPARATION | WFI | 2026-07-18 | 2026-07-21 | 0 | 0 |  |  |  | PASSED | FALSE |  | synced
2026-07-16 | WFI09 | SV216.10 | PQ3-Day4 | WP-26-0113 | TRUE | 16-1-105 | Building 16 | WASHING/TUNNEL-01 | WFI | 2026-07-18 | 2026-07-21 | 0 | 0 |  |  |  | PASSED | FALSE |  | synced
2026-07-17 | WFI10 | POU HE216.04 | PQ3-Day5 | WP-26-0114 | TRUE | 16-1-114 | Building 16 | COMPOUNDING-02 | WFI | 2026-07-18 | 2026-07-21 | 0 | 0 |  |  |  | PASSED | FALSE |  | synced
2026-07-17 | WFI11 | POU HE216.05 | PQ3-Day5 | WP-26-0114 | TRUE | 16-1-114 | Building 16 | COMPOUNDING-02 | WFI | 2026-07-18 | 2026-07-21 | 0 | 0 |  |  |  | PASSED | FALSE |  | synced
2026-07-20 | GWFI01 | V12-4 | PQ3-Day1 | WP-26-0115 | TRUE | 16-2-010 | Building 16 | AFTER WFI GENERATOR | WFI | 2026-07-21 | 2026-07-24 | 0 | 0 |  |  |  | PASSED | FALSE |  | synced
2026-07-20 | GWFI02 | SV213.01 | PQ3-Day1 | WP-26-0115 | TRUE | 16-2-010 | Building 16 | AFTER STORAGE TANK | WFI | 2026-07-21 | 2026-07-24 | 0 | 0 |  |  |  | PASSED | FALSE |  | synced
2026-07-20 | GWFI03 | SV217.01 | PQ3-Day1 | WP-26-0115 | TRUE | 16-2-010 | Building 16 | RETURN LOOP | WFI | 2026-07-21 | 2026-07-24 | 0 | 0 |  |  |  | PASSED | FALSE |  | synced
2026-07-20 | WFI07 | SV216.02 | PQ3-Day1 | WP-26-0115 | TRUE | 16-1-098 | Building 16 | CIP/SIP | WFI | 2026-07-21 | 2026-07-24 | 0 | 0 |  |  |  | PASSED | FALSE |  | synced
2026-07-20 | WFI08 | SV216.04 | PQ3-Day1 | WP-26-0115 | TRUE | 16-1-098 | Building 16 | CIP/SIP | WFI | 2026-07-21 | 2026-07-24 | 0 | 0 |  |  |  | PASSED | FALSE |  | synced
2026-07-21 | WFI03 | SV216.03 | PQ3-Day2 | WP-26-0116 | TRUE | 16-1-096 | Building 16 | WASHING/TUNNEL-02 | WFI | 2026-07-21 | 2026-07-24 | 0 | 0 |  |  |  | PASSED | FALSE |  | synced
2026-07-21 | WFI04 | POU HE216.03 | PQ3-Day2 | WP-26-0116 | TRUE | 16-1-082 | Building 16 | WASHING | WFI | 2026-07-21 | 2026-07-24 | 0 | 0 |  |  |  | PASSED | FALSE |  | synced
2026-07-21 | WFI05 | SV216.06 | PQ3-Day2 | WP-26-0116 | TRUE | 16-1-082 | Building 16 | WASHING | WFI | 2026-07-21 | 2026-07-24 | 0 | 0 |  |  |  | PASSED | FALSE |  | synced
2026-07-22 | WFI01 | POU HE216.01 | PQ3-Day3 | WP-26-0117 | TRUE | 16-1-107 | Building 16 | COMPOUNDING-01 | WFI | 2026-07-23 | 2026-07-27 | 0 | 0 |  |  |  | PASSED | FALSE |  | synced
2026-07-22 | WFI02 | POU HE216.02 | PQ3-Day3 | WP-26-0117 | TRUE | 16-1-107 | Building 16 | COMPOUNDING-01 | WFI | 2026-07-23 | 2026-07-27 | 0 | 0 |  |  |  | PASSED | FALSE |  | synced
2026-07-23 | WFI06 | SV216.05 | PQ3-Day4 | WP-26-0118 | TRUE | 16-1-110 | Building 16 | DISINFECTANT PREPARATION | WFI | 2026-07-23 | 2026-07-27 | 0 | 0 |  |  |  | PASSED | FALSE |  | synced
2026-07-23 | WFI09 | SV216.10 | PQ3-Day4 | WP-26-0118 | TRUE | 16-1-105 | Building 16 | WASHING/TUNNEL-01 | WFI | 2026-07-23 | 2026-07-27 | 0 | 0 |  |  |  | PASSED | FALSE |  | synced
2026-07-24 | WFI10 | POU HE216.04 | PQ3-Day5 | WP-26-0119 | TRUE | 16-1-114 | Building 16 | COMPOUNDING-02 | WFI | 2026-07-25 | 2026-07-28 | 0 | 0 |  |  |  | PASSED | FALSE |  | synced
2026-07-24 | WFI11 | POU HE216.05 | PQ3-Day5 | WP-26-0119 | TRUE | 16-1-114 | Building 16 | COMPOUNDING-02 | WFI | 2026-07-25 | 2026-07-28 | 0 | 0 |  |  |  | PASSED | FALSE |  | synced
2026-08-03 | GWFI01 | V12-4 | PQ3-Day1 | WP-26-0120 | TRUE | 16-2-010 | Building 16 | AFTER WFI GENERATOR | WFI | 2026-08-04 | 2026-08-08 | 0 | 0 |  |  |  | PASSED | FALSE |  | synced
2026-08-03 | GWFI02 | SV213.01 | PQ3-Day1 | WP-26-0120 | TRUE | 16-2-010 | Building 16 | AFTER STORAGE TANK | WFI | 2026-08-04 | 2026-08-08 | 0 | 0 |  |  |  | PASSED | FALSE |  | synced
2026-08-03 | GWFI03 | SV217.01 | PQ3-Day1 | WP-26-0120 | TRUE | 16-2-010 | Building 16 | RETURN LOOP | WFI | 2026-08-04 | 2026-08-08 | 0 | 0 |  |  |  | PASSED | FALSE |  | synced
2026-08-03 | WFI07 | SV216.02 | PQ3-Day1 | WP-26-0120 | TRUE | 16-1-098 | Building 16 | CIP/SIP | WFI | 2026-08-04 | 2026-08-08 | 0 | 0 |  |  |  | PASSED | FALSE |  | synced
2026-08-03 | WFI08 | SV216.04 | PQ3-Day1 | WP-26-0120 | TRUE | 16-1-098 | Building 16 | CIP/SIP | WFI | 2026-08-04 | 2026-08-08 | 0 | 0 |  |  |  | PASSED | FALSE |  | synced
2026-08-04 | WFI03 | SV216.03 | PQ3-Day2 | WP-26-0121 | TRUE | 16-1-096 | Building 16 | WASHING/TUNNEL-02 | WFI | 2026-08-04 | 2026-08-08 | 0 | 0 |  |  |  | PASSED | FALSE |  | synced
2026-08-04 | WFI04 | POU HE216.03 | PQ3-Day2 | WP-26-0121 | TRUE | 16-1-082 | Building 16 | WASHING | WFI | 2026-08-04 | 2026-08-08 | 0 | 0 |  |  |  | PASSED | FALSE |  | synced
2026-08-04 | WFI05 | SV216.06 | PQ3-Day2 | WP-26-0121 | TRUE | 16-1-082 | Building 16 | WASHING | WFI | 2026-08-04 | 2026-08-08 | 0 | 0 |  |  |  | PASSED | FALSE |  | synced
2026-08-05 | WFI01 | POU HE216.01 | PQ3-Day3 | WP-26-0122 | TRUE | 16-1-107 | Building 16 | COMPOUNDING-01 | WFI | 2026-08-07 | 2026-08-10 | 0 | 0 |  |  |  | PASSED | FALSE |  | synced
2026-08-05 | WFI02 | POU HE216.02 | PQ3-Day3 | WP-26-0122 | TRUE | 16-1-107 | Building 16 | COMPOUNDING-01 | WFI | 2026-08-07 | 2026-08-10 | 0 | 0 |  |  |  | PASSED | FALSE |  | synced
2026-08-06 | WFI06 | SV216.05 | PQ3-Day4 | WP-26-0123 | TRUE | 16-1-110 | Building 16 | DISINFECTANT PREPARATION | WFI | 2026-08-07 | 2026-08-10 | 0 | 0 |  |  |  | PASSED | FALSE |  | synced
2026-08-06 | WFI09 | SV216.10 | PQ3-Day4 | WP-26-0123 | TRUE | 16-1-105 | Building 16 | WASHING/TUNNEL-01 | WFI | 2026-08-07 | 2026-08-10 | 0 | 0 |  |  |  | PASSED | FALSE |  | synced
2026-08-07 | WFI10 | POU HE216.04 | PQ3-Day5 | WP-26-0124 | TRUE | 16-1-114 | Building 16 | COMPOUNDING-02 | WFI | 2026-08-07 | 2026-08-10 | 0 | 0 |  |  |  | PASSED | FALSE |  | synced
2026-08-07 | WFI11 | POU HE216.05 | PQ3-Day5 | WP-26-0124 | TRUE | 16-1-114 | Building 16 | COMPOUNDING-02 | WFI | 2026-08-07 | 2026-08-10 | 0 | 0 |  |  |  | PASSED | FALSE |  | synced
2026-08-10 | GWFI01 | V12-4 | PQ3-Day1 | WP-26-0125 | TRUE | 16-2-010 | Building 16 | AFTER WFI GENERATOR | WFI | 2026-08-12 | 2026-08-15 | 0 | 0 |  |  |  | PASSED | FALSE |  | synced
2026-08-10 | GWFI02 | SV213.01 | PQ3-Day1 | WP-26-0125 | TRUE | 16-2-010 | Building 16 | AFTER STORAGE TANK | WFI | 2026-08-12 | 2026-08-15 | 0 | 0 |  |  |  | PASSED | FALSE |  | synced
2026-08-10 | GWFI03 | SV217.01 | PQ3-Day1 | WP-26-0125 | TRUE | 16-2-010 | Building 16 | RETURN LOOP | WFI | 2026-08-12 | 2026-08-15 | 0 | 0 |  |  |  | PASSED | FALSE |  | synced
2026-08-10 | WFI07 | SV216.02 | PQ3-Day1 | WP-26-0125 | TRUE | 16-1-098 | Building 16 | CIP/SIP | WFI | 2026-08-12 | 2026-08-15 | 0 | 0 |  |  |  | PASSED | FALSE |  | synced
2026-08-10 | WFI08 | SV216.04 | PQ3-Day1 | WP-26-0125 | TRUE | 16-1-098 | Building 16 | CIP/SIP | WFI | 2026-08-12 | 2026-08-15 | 0 | 0 |  |  |  | PASSED | FALSE |  | synced
2026-08-11 | WFI03 | SV216.03 | PQ3-Day2 | WP-26-0126 | TRUE | 16-1-096 | Building 16 | WASHING/TUNNEL-02 | WFI | 2026-08-12 | 2026-08-15 | 0 | 0 |  |  |  | PASSED | FALSE |  | synced
2026-08-11 | WFI04 | POU HE216.03 | PQ3-Day2 | WP-26-0126 | TRUE | 16-1-082 | Building 16 | WASHING | WFI | 2026-08-12 | 2026-08-15 | 0 | 0 |  |  |  | PASSED | FALSE |  | synced
2026-08-11 | WFI05 | SV216.06 | PQ3-Day2 | WP-26-0126 | TRUE | 16-1-082 | Building 16 | WASHING | WFI | 2026-08-12 | 2026-08-15 | 0 | 0 |  |  |  | PASSED | FALSE |  | synced
2026-08-13 | WFI01 | POU HE216.01 | PQ3-Day4 | WP-26-0127 | TRUE | 16-1-107 | Building 16 | COMPOUNDING-01 | WFI | 2026-08-15 | 2026-08-18 | 0 | 0 |  |  |  | PASSED | FALSE |  | synced
2026-08-13 | WFI02 | POU HE216.02 | PQ3-Day4 | WP-26-0127 | TRUE | 16-1-107 | Building 16 | COMPOUNDING-01 | WFI | 2026-08-15 | 2026-08-18 | 0 | 0 |  |  |  | PASSED | FALSE |  | synced
2026-08-13 | WFI06 | SV216.05 | PQ3-Day4 | WP-26-0127 | TRUE | 16-1-110 | Building 16 | DISINFECTANT PREPARATION | WFI | 2026-08-15 | 2026-08-18 | 0 | 0 |  |  |  | PASSED | FALSE |  | synced
2026-08-13 | WFI09 | SV216.10 | PQ3-Day4 | WP-26-0127 | TRUE | 16-1-105 | Building 16 | WASHING/TUNNEL-01 | WFI | 2026-08-15 | 2026-08-18 | 0 | 0 |  |  |  | PASSED | FALSE |  | synced
2026-08-14 | WFI10 | POU HE216.04 | PQ3-Day5 | WP-26-0128 | TRUE | 16-1-114 | Building 16 | COMPOUNDING-02 | WFI | 2026-08-15 | 2026-08-18 | 0 | 0 |  |  |  | PASSED | FALSE |  | synced
2026-08-14 | WFI11 | POU HE216.05 | PQ3-Day5 | WP-26-0128 | TRUE | 16-1-114 | Building 16 | COMPOUNDING-02 | WFI | 2026-08-15 | 2026-08-18 | 0 | 0 |  |  |  | PASSED | FALSE |  | synced
2026-08-17 | GWFI01 | V12-4 | PQ3-Day1 | WP-26-0129 | TRUE | 16-2-010 | Building 16 | AFTER WFI GENERATOR | WFI | 2026-08-19 | 2026-08-22 | 0 | 0 |  |  |  | PASSED | FALSE |  | synced
2026-08-17 | GWFI02 | SV213.01 | PQ3-Day1 | WP-26-0129 | TRUE | 16-2-010 | Building 16 | AFTER STORAGE TANK | WFI | 2026-08-19 | 2026-08-22 | 0 | 0 |  |  |  | PASSED | FALSE |  | synced
2026-08-17 | GWFI03 | SV217.01 | PQ3-Day1 | WP-26-0129 | TRUE | 16-2-010 | Building 16 | RETURN LOOP | WFI | 2026-08-19 | 2026-08-22 | 0 | 0 |  |  |  | PASSED | FALSE |  | synced
2026-08-17 | WFI07 | SV216.02 | PQ3-Day1 | WP-26-0129 | TRUE | 16-1-098 | Building 16 | CIP/SIP | WFI | 2026-08-19 | 2026-08-22 | 0 | 0 |  |  |  | PASSED | FALSE |  | synced
2026-08-17 | WFI08 | SV216.04 | PQ3-Day1 | WP-26-0129 | TRUE | 16-1-098 | Building 16 | CIP/SIP | WFI | 2026-08-19 | 2026-08-22 | 0 | 0 |  |  |  | PASSED | FALSE |  | synced
2026-08-18 | WFI03 | SV216.03 | PQ3-Day2 | WP-26-0130 | TRUE | 16-1-096 | Building 16 | WASHING/TUNNEL-02 | WFI | 2026-08-19 | 2026-08-22 | 0 | 0 |  |  |  | PASSED | FALSE |  | synced
2026-08-18 | WFI04 | POU HE216.03 | PQ3-Day2 | WP-26-0130 | TRUE | 16-1-082 | Building 16 | WASHING | WFI | 2026-08-19 | 2026-08-22 | 0 | 0 |  |  |  | PASSED | FALSE |  | synced
2026-08-18 | WFI05 | SV216.06 | PQ3-Day2 | WP-26-0130 | TRUE | 16-1-082 | Building 16 | WASHING | WFI | 2026-08-19 | 2026-08-22 | 0 | 0 |  |  |  | PASSED | FALSE |  | synced
2026-08-19 | WFI01 | POU HE216.01 | PQ3-Day4 | WP-26-0131 | TRUE | 16-1-107 | Building 16 | COMPOUNDING-01 | WFI | 2026-08-19 | 2026-08-22 | 0 | 0 |  |  |  | PASSED | FALSE |  | synced
2026-08-19 | WFI02 | POU HE216.02 | PQ3-Day4 | WP-26-0131 | TRUE | 16-1-107 | Building 16 | COMPOUNDING-01 | WFI | 2026-08-19 | 2026-08-22 | 0 | 0 |  |  |  | PASSED | FALSE |  | synced
2026-08-20 | WFI06 | SV216.05 | PQ3-Day4 | WP-26-0132 | TRUE | 16-1-110 | Building 16 | DISINFECTANT PREPARATION | WFI | 2026-08-22 | 2026-08-25 | 0 | 0 |  |  |  | PASSED | FALSE |  | synced
2026-08-20 | WFI09 | SV216.10 | PQ3-Day4 | WP-26-0132 | TRUE | 16-1-105 | Building 16 | WASHING/TUNNEL-01 | WFI | 2026-08-22 | 2026-08-25 | 0 | 0 |  |  |  | PASSED | FALSE |  | synced
2026-08-21 | WFI10 | POU HE216.04 | PQ3-Day5 | WP-26-0133 | TRUE | 16-1-114 | Building 16 | COMPOUNDING-02 | WFI | 2026-08-22 | 2026-08-25 | 0 | 0 |  |  |  | PASSED | FALSE |  | synced
2026-08-21 | WFI11 | POU HE216.05 | PQ3-Day5 | WP-26-0133 | TRUE | 16-1-114 | Building 16 | COMPOUNDING-02 | WFI | 2026-08-22 | 2026-08-25 | 0 | 0 |  |  |  | PASSED | FALSE |  | synced
2026-08-24 | GWFI01 | V12-4 | PQ3-Day1 | WP-26-0134 | TRUE | 16-2-010 | Building 16 | AFTER WFI GENERATOR | WFI | 2026-08-26 | 2026-08-29 | 0 | 0 |  |  |  | PASSED | FALSE |  | synced
2026-08-24 | GWFI02 | SV213.01 | PQ3-Day1 | WP-26-0134 | TRUE | 16-2-010 | Building 16 | AFTER STORAGE TANK | WFI | 2026-08-26 | 2026-08-29 | 0 | 0 |  |  |  | PASSED | FALSE |  | synced
2026-08-24 | GWFI03 | SV217.01 | PQ3-Day1 | WP-26-0134 | TRUE | 16-2-010 | Building 16 | RETURN LOOP | WFI | 2026-08-26 | 2026-08-29 | 0 | 0 |  |  |  | PASSED | FALSE |  | synced
2026-08-24 | WFI07 | SV216.02 | PQ3-Day1 | WP-26-0134 | TRUE | 16-1-098 | Building 16 | CIP/SIP | WFI | 2026-08-26 | 2026-08-29 | 0 | 0 |  |  |  | PASSED | FALSE |  | synced
2026-08-24 | WFI08 | SV216.04 | PQ3-Day1 | WP-26-0134 | TRUE | 16-1-098 | Building 16 | CIP/SIP | WFI | 2026-08-26 | 2026-08-29 | 0 | 0 |  |  |  | PASSED | FALSE |  | synced
2026-08-25 | WFI03 | SV216.03 | PQ3-Day2 | WP-26-0135 | TRUE | 16-1-096 | Building 16 | WASHING/TUNNEL-02 | WFI | 2026-08-26 | 2026-08-29 | 0 | 0 |  |  |  | PASSED | FALSE |  | synced
2026-08-25 | WFI04 | POU HE216.03 | PQ3-Day2 | WP-26-0135 | TRUE | 16-1-082 | Building 16 | WASHING | WFI | 2026-08-26 | 2026-08-29 | 0 | 0 |  |  |  | PASSED | FALSE |  | synced
2026-08-25 | WFI05 | SV216.06 | PQ3-Day2 | WP-26-0135 | TRUE | 16-1-082 | Building 16 | WASHING | WFI | 2026-08-26 | 2026-08-29 | 0 | 0 |  |  |  | PASSED | FALSE |  | synced
2026-08-26 | WFI01 | POU HE216.01 | PQ3-Day4 | WP-26-0136 | TRUE | 16-1-107 | Building 16 | COMPOUNDING-01 | WFI | 2026-08-26 | 2026-08-29 | 0 | 0 |  |  |  | PASSED | FALSE |  | synced
2026-08-26 | WFI02 | POU HE216.02 | PQ3-Day4 | WP-26-0136 | TRUE | 16-1-107 | Building 16 | COMPOUNDING-01 | WFI | 2026-08-26 | 2026-08-29 | 0 | 0 |  |  |  | PASSED | FALSE |  | synced
2026-08-27 | WFI06 | SV216.05 | PQ3-Day4 | WP-26-0137 | TRUE | 16-1-110 | Building 16 | DISINFECTANT PREPARATION | WFI | 2026-08-29 | 2026-09-01 | 0 | 0 |  |  |  | PASSED | FALSE |  | synced
2026-08-27 | WFI09 | SV216.10 | PQ3-Day4 | WP-26-0137 | TRUE | 16-1-105 | Building 16 | WASHING/TUNNEL-01 | WFI | 2026-08-29 | 2026-09-01 | 0 | 0 |  |  |  | PASSED | FALSE |  | synced
2026-08-28 | WFI10 | POU HE216.04 | PQ3-Day5 | WP-26-0138 | TRUE | 16-1-114 | Building 16 | COMPOUNDING-02 | WFI | 2026-08-29 | 2026-09-01 | 0 | 0 |  |  |  | PASSED | FALSE |  | synced
2026-08-28 | WFI11 | POU HE216.05 | PQ3-Day5 | WP-26-0138 | TRUE | 16-1-114 | Building 16 | COMPOUNDING-02 | WFI | 2026-08-29 | 2026-09-01 | 0 | 0 |  |  |  | PASSED | FALSE |  | synced
2026-08-31 | GWFI01 | V12-4 | PQ3-Day1 | WP-26-0139 | TRUE | 16-2-010 | Building 16 | AFTER WFI GENERATOR | WFI | 2026-09-02 | 2026-09-05 | 0 | 0 |  |  |  | PASSED | FALSE |  | error
2026-08-31 | GWFI02 | SV213.01 | PQ3-Day1 | WP-26-0139 | TRUE | 16-2-010 | Building 16 | AFTER STORAGE TANK | WFI | 2026-09-02 | 2026-09-05 | 0 | 0 |  |  |  | PASSED | FALSE |  | error
2026-08-31 | GWFI03 | SV217.01 | PQ3-Day1 | WP-26-0139 | TRUE | 16-2-010 | Building 16 | RETURN LOOP | WFI | 2026-09-02 | 2026-09-05 | 0 | 0 |  |  |  | PASSED | FALSE |  | error
2026-08-31 | WFI07 | SV216.02 | PQ3-Day1 | WP-26-0139 | TRUE | 16-1-098 | Building 16 | CIP/SIP | WFI | 2026-09-02 | 2026-09-05 | 0 | 0 |  |  |  | PASSED | FALSE |  | error
2026-08-31 | WFI08 | SV216.04 | PQ3-Day1 | WP-26-0139 | TRUE | 16-1-098 | Building 16 | CIP/SIP | WFI | 2026-09-02 | 2026-09-05 | 0 | 0 |  |  |  | PASSED | FALSE |  | error
2026-09-01 | WFI03 | SV216.03 | PQ3-Day2 | WP-26-0140 | TRUE | 16-1-096 | Building 16 | WASHING/TUNNEL-02 | WFI | 2026-09-02 | 2026-09-05 | 0 | 0 |  |  |  | PASSED | FALSE |  | synced
2026-09-01 | WFI04 | POU HE216.03 | PQ3-Day2 | WP-26-0140 | TRUE | 16-1-082 | Building 16 | WASHING | WFI | 2026-09-02 | 2026-09-05 | 0 | 0 |  |  |  | PASSED | FALSE |  | synced
2026-09-01 | WFI05 | SV216.06 | PQ3-Day2 | WP-26-0140 | TRUE | 16-1-082 | Building 16 | WASHING | WFI | 2026-09-02 | 2026-09-05 | 0 | 0 |  |  |  | PASSED | FALSE |  | synced
2026-09-02 | WFI01 | POU HE216.01 | PQ3-Day4 | WP-26-0141 | TRUE | 16-1-107 | Building 16 | COMPOUNDING-01 | WFI | 2026-09-02 | 2026-09-05 | 0 | 0 |  |  |  | PASSED | FALSE |  | synced
2026-09-02 | WFI02 | POU HE216.02 | PQ3-Day4 | WP-26-0141 | TRUE | 16-1-107 | Building 16 | COMPOUNDING-01 | WFI | 2026-09-02 | 2026-09-05 | 0 | 0 |  |  |  | PASSED | FALSE |  | synced
2026-09-03 | WFI06 | SV216.05 | PQ3-Day4 |  | FALSE | 16-1-110 | Building 16 | DISINFECTANT PREPARATION | WFI | 2026-09-05 | [6 empty] | PASSED | FALSE |  | error
2026-09-03 | WFI09 | SV216.10 | PQ3-Day4 |  | FALSE | 16-1-105 | Building 16 | WASHING/TUNNEL-01 | WFI | 2026-09-05 | [6 empty] | PASSED | FALSE |  | error
2026-09-04 | WFI10 | POU HE216.04 | PQ3-Day5 |  | FALSE | 16-1-114 | Building 16 | COMPOUNDING-02 | WFI | 2026-09-05 | [6 empty] | PASSED | FALSE |  | error
2026-09-04 | WFI11 | POU HE216.05 | PQ3-Day5 |  | FALSE | 16-1-114 | Building 16 | COMPOUNDING-02 | WFI | 2026-09-05 | [6 empty] | PASSED | FALSE |  | error
2026-09-07 | GWFI01 | V12-4 | PQ3-Day1 |  | FALSE | 16-2-010 | Building 16 | AFTER WFI GENERATOR | WFI | 2026-09-08 | [6 empty] | PASSED | FALSE
2026-09-07 | GWFI02 | SV213.01 | PQ3-Day1 |  | FALSE | 16-2-010 | Building 16 | AFTER STORAGE TANK | WFI | 2026-09-08 | [6 empty] | PASSED | FALSE
2026-09-07 | GWFI03 | SV217.01 | PQ3-Day1 |  | FALSE | 16-2-010 | Building 16 | RETURN LOOP | WFI | 2026-09-08 | [6 empty] | PASSED | FALSE
2026-09-07 | WFI07 | SV216.02 | PQ3-Day1 |  | FALSE | 16-1-098 | Building 16 | CIP/SIP | WFI | 2026-09-08 | [6 empty] | PASSED | FALSE
2026-09-07 | WFI08 | SV216.04 | PQ3-Day1 |  | FALSE | 16-1-098 | Building 16 | CIP/SIP | WFI | 2026-09-08 | [6 empty] | PASSED | FALSE
2026-09-08 | WFI03 | SV216.03 | PQ3-Day2 |  | FALSE | 16-1-096 | Building 16 | WASHING/TUNNEL-02 | WFI | 2026-09-09 | [6 empty] | PASSED | FALSE
2026-09-08 | WFI04 | POU HE216.03 | PQ3-Day2 |  | FALSE | 16-1-082 | Building 16 | WASHING | WFI | 2026-09-09 | [6 empty] | PASSED | FALSE
2026-09-08 | WFI05 | SV216.06 | PQ3-Day2 |  | FALSE | 16-1-082 | Building 16 | WASHING | WFI | 2026-09-10 | [6 empty] | PASSED | FALSE
2026-09-09 | WFI01 | POU HE216.01 | PQ3-Day4 |  | FALSE | 16-1-107 | Building 16 | COMPOUNDING-01 | WFI | 2026-09-10 | [6 empty] | PASSED | FALSE
2026-09-09 | WFI02 | POU HE216.02 | PQ3-Day4 |  | FALSE | 16-1-107 | Building 16 | COMPOUNDING-01 | WFI | 2026-09-10 | [6 empty] | PASSED | FALSE
2026-09-10 | WFI06 | SV216.05 | PQ3-Day4 |  | FALSE | 16-1-110 | Building 16 | DISINFECTANT PREPARATION | WFI | 2026-09-11 | [6 empty] | PASSED | FALSE
2026-09-10 | WFI09 | SV216.10 | PQ3-Day4 |  | FALSE | 16-1-105 | Building 16 | WASHING/TUNNEL-01 | WFI | 2026-09-11 | [6 empty] | PASSED | FALSE
2026-09-11 | WFI10 | POU HE216.04 | PQ3-Day5 |  | FALSE | 16-1-114 | Building 16 | COMPOUNDING-02 | WFI | 2026-09-12 | [6 empty] | PASSED | FALSE
2026-09-11 | WFI11 | POU HE216.05 | PQ3-Day5 |  | FALSE | 16-1-114 | Building 16 | COMPOUNDING-02 | WFI | 2026-09-12 | [6 empty] | PASSED | FALSE
Formulas:
performedDate = [samplingDate]+2
performedDate = [samplingDate]
determinedDate = [samplingDate]+5

## _rpp2_registry (hidden)
worksheetNo | rpp2Sheet | sourceSheet | updatedAt
WT-26-0073 | records_pw_prw | prw-pw | 2026-06-10T01:27:43.887Z
WT-26-0074 | records_pw_prw | prw-pw | 2026-07-10T09:03:33.159Z
WT-26-0075 | records_pw_prw | prw-pw | 2026-07-10T09:03:37.983Z
WT-26-0076 | records_pw_prw | prw-pw | 2026-06-10T06:41:12.687Z
WT-26-0077 | records_pw_prw | prw-pw | 2026-08-07T01:39:51.882Z
WT-26-0078 | records_pw_prw | prw-pw | 2026-06-10T06:41:19.852Z
WT-26-0079 | records_pw_prw | prw-pw | 2026-06-10T06:41:23.742Z
WT-26-0080 | records_pw_prw | prw-pw | 2026-06-11T03:43:51.141Z
WT-26-0081 | records_pw_prw | prw-pw | 2026-07-10T09:03:42.399Z
WT-26-0070 | records_pw_prw | prw-pw | 2026-07-10T09:03:27.694Z
WT-26-0071 | records_pw_prw | prw-pw | 2026-06-09T08:57:15.207Z
WT-26-0072 | records_pw_prw | prw-pw | 2026-06-09T08:22:33.895Z
WT-26-0082 | records_pw_prw | prw-pw | 2026-06-15T02:31:42.832Z
WP-26-0080 | records_wfi | wfi-pus | 2026-06-09T08:23:25.858Z
WP-26-0081 | records_wfi | wfi-pus | 2026-06-11T08:30:51.397Z
WP-26-0082 | records_wfi | wfi-pus | 2026-06-11T08:30:54.491Z
WP-26-0083 | records_wfi | wfi-pus | 2026-06-11T08:30:58.356Z
WP-26-0084 | records_wfi | wfi-pus | 2026-06-11T08:31:01.536Z
WP-26-0085 | records_wfi | wfi-pus | 2026-06-16T08:15:29.390Z
WP-26-0086 | records_wfi | wfi-pus | 2026-06-16T08:15:36.840Z
WP-26-0087 | records_wfi | wfi-pus | 2026-07-11T07:27:11.060Z
WP-26-0088 | records_wfi | wfi-pus | 2026-06-22T04:13:44.890Z
WP-26-0089 | records_wfi | wfi-pus | 2026-06-22T04:13:48.948Z
WT-26-0083 | records_pw_prw | prw-pw | 2026-07-10T09:03:46.752Z
WP-26-0090 | records_wfi | wfi-pus | 2026-06-22T04:13:52.875Z
WT-26-0084 | records_pw_prw | prw-pw | 2026-06-29T01:52:08.209Z
WT-26-0085 | records_pw_prw | prw-pw | 2026-06-22T04:11:48.300Z
WP-26-0091 | records_wfi | wfi-pus | 2026-06-22T04:13:56.648Z
WP-26-0092 | records_wfi | wfi-pus | 2026-07-11T07:27:15.431Z
WT-26-0086 | records_pw_prw | prw-pw | 2026-06-29T01:52:13.052Z
WT-26-0087 | records_pw_prw | prw-pw | 2026-06-29T01:52:16.238Z
WP-26-0093 | records_wfi | wfi-pus | 2026-06-29T01:53:58.125Z
WP-26-0094 | records_wfi | wfi-pus | 2026-06-29T01:54:02.837Z
WP-26-0095 | records_wfi | wfi-pus | 2026-07-01T02:37:29.084Z
WT-26-0088 | records_pw_prw | prw-pw | 2026-06-29T01:52:20.545Z
WT-26-0089 | records_pw_prw | prw-pw | 2026-07-10T09:03:50.633Z
WT-26-0090 | records_pw_prw | prw-pw | 2026-07-10T09:03:54.756Z
WT-26-0091 | records_pw_prw | prw-pw | 2026-07-06T09:05:29.253Z
WP-26-0096 | records_wfi | wfi-pus | 2026-07-01T02:37:34.237Z
WP-26-0097 | records_wfi | wfi-pus | 2026-07-11T07:27:19.117Z
WP-26-0098 | records_wfi | wfi-pus | 2026-07-06T07:54:12.431Z
WP-26-0099 | records_wfi | wfi-pus | 2026-07-06T07:54:21.692Z
WP-26-0100 | records_wfi | wfi-pus | 2026-07-06T07:54:28.195Z
WT-26-0092 | records_pw_prw | prw-pw | 2026-07-10T09:03:58.883Z
WT-26-0093 | records_pw_prw | prw-pw | 2026-08-07T01:39:55.514Z
WP-26-0101 | records_wfi | wfi-pus | 2026-07-09T07:22:09.089Z
WP-26-0102 | records_wfi | wfi-pus | 2026-07-11T07:27:23.475Z
WP-26-0103 | records_wfi | wfi-pus | 2026-07-09T07:22:18.395Z
WT-26-0094 | records_pw_prw | prw-pw | 2026-07-08T07:01:19.994Z
WT-26-0095 | records_pw_prw | prw-pw | 2026-07-06T09:05:47.975Z
WP-26-0104 | records_wfi | wfi-pus | 2026-07-06T07:54:51.772Z
WT-26-0096 | records_pw_prw | prw-pw | 2026-07-08T07:01:23.379Z
WT-26-0098 | records_pw_prw | prw-pw | 2026-07-08T07:23:07.638Z
WT-26-0099 | records_pw_prw | prw-pw | 2026-07-14T10:08:04.496Z
WP-26-0105 | records_wfi | wfi-pus | 2026-07-11T07:27:27.484Z
WP-26-0106 | records_wfi | wfi-pus | 2026-07-11T07:27:33.311Z
WP-26-0107 | records_wfi | wfi-pus | 2026-07-16T09:35:49.214Z
WP-26-0108 | records_wfi | wfi-pus | 2026-07-16T09:35:55.125Z
WT-26-0100 | records_pw_prw | prw-pw | 2026-07-14T10:08:09.779Z
WP-26-0109 | records_wfi | wfi-pus | 2026-07-16T09:36:02.044Z
WT-26-0101 | records_pw_prw | prw-pw | 2026-07-21T10:42:22.121Z
WT-26-0102 | records_pw_prw | prw-pw | 2026-07-18T08:13:31.617Z
WP-26-0110 | records_wfi | wfi-pus | 2026-07-18T08:12:24.315Z
WP-26-0111 | records_wfi | wfi-pus | 2026-07-21T09:59:31.211Z
WP-26-0112 | records_wfi | wfi-pus | 2026-07-21T09:59:35.626Z
WP-26-0113 | records_wfi | wfi-pus | 2026-07-21T09:59:41.337Z
WP-26-0114 | records_wfi | wfi-pus | 2026-07-21T09:59:46.234Z
WT-26-0103 | records_pw_prw | prw-pw | 2026-07-22T12:03:20.388Z
WT-26-0104 | records_pw_prw | prw-pw | 2026-07-22T12:03:26.305Z
WT-26-0105 | records_pw_prw | prw-pw | 2026-07-22T12:03:31.687Z
WP-26-0115 | records_wfi | wfi-pus | 2026-07-27T01:24:27.999Z
WP-26-0116 | records_wfi | wfi-pus | 2026-07-27T01:24:33.374Z
WT-26-0106 | records_pw_prw | prw-pw | 2026-07-27T01:17:10.486Z
WT-26-0107 | records_pw_prw | prw-pw | 2026-08-07T01:40:01.847Z
WT-26-0108 | records_pw_prw | prw-pw | 2026-07-21T10:42:44.097Z
WT-26-0109 | records_pw_prw | prw-pw | 2026-07-31T04:32:58.878Z
WP-26-0117 | records_wfi | wfi-pus | 2026-08-07T02:26:16.444Z
WP-26-0118 | records_wfi | wfi-pus | 2026-08-07T02:26:20.012Z
WT-26-0110 | records_pw_prw | prw-pw | 2026-07-27T01:23:25.444Z
WT-26-0111 | records_pw_prw | prw-pw | 2026-07-27T03:16:43.781Z
WT-26-0112 | records_pw_prw | prw-pw | 2026-07-31T04:33:07.344Z
WT-26-0113 | records_pw_prw | prw-pw | 2026-07-27T01:23:28.140Z
WP-26-0119 | records_wfi | wfi-pus | 2026-08-07T02:26:23.490Z
WT-26-0114 | records_pw_prw | prw-pw | 2026-07-31T04:33:03.708Z
WT-26-0115 | records_pw_prw | prw-pw | 2026-08-07T01:40:06.348Z
WT-26-0116 | records_pw_prw | prw-pw | 2026-08-07T01:40:10.363Z
WT-26-0117 | records_pw_prw | prw-pw | 2026-08-07T01:40:13.788Z
WT-26-0118 | records_pw_prw | prw-pw | 2026-08-07T01:40:17.323Z
WT-26-0119 | records_pw_prw | prw-pw | 2026-08-07T01:40:21.383Z
WT-26-0120 | records_pw_prw | prw-pw | 2026-08-07T01:40:25.014Z
WT-26-0121 | records_pw_prw | prw-pw | 2026-08-11T08:39:46.539Z
WT-26-0122 | records_pw_prw | prw-pw | 2026-08-11T08:39:51.186Z
WT-26-0123 | records_pw_prw | prw-pw | 2026-08-07T01:40:36.042Z
WT-26-0124 | records_pw_prw | prw-pw | 2026-08-14T01:30:26.635Z
WT-26-0125 | records_pw_prw | prw-pw | 2026-08-11T08:40:00.477Z
WT-26-0126 | records_pw_prw | prw-pw | 2026-08-11T08:40:06.111Z
WT-26-0127 | records_pw_prw | prw-pw | 2026-08-11T08:40:10.395Z
WP-26-0120 | records_wfi | wfi-pus | 2026-08-12T08:18:35.937Z
WP-26-0121 | records_wfi | wfi-pus | 2026-08-12T08:18:40.372Z
WP-26-0122 | records_wfi | wfi-pus | 2026-08-12T08:18:43.663Z
WP-26-0123 | records_wfi | wfi-pus | 2026-08-12T08:18:47.237Z
WP-26-0124 | records_wfi | wfi-pus | 2026-08-12T08:18:50.911Z
WT-26-0128 | records_pw_prw | prw-pw | 2026-08-11T08:40:12.937Z
WP-26-0125 | records_wfi | wfi-pus | 2026-08-15T08:14:01.736Z
WP-26-0126 | records_wfi | wfi-pus | 2026-08-12T08:18:55.663Z
WT-26-0129 | records_pw_prw | prw-pw | 2026-08-15T08:11:38.410Z
WT-26-0130 | records_pw_prw | prw-pw | 2026-08-15T08:11:42.632Z
WT-26-0131 | records_pw_prw | prw-pw | 2026-08-15T08:11:46.749Z
WT-26-0132 | records_pw_prw | prw-pw | 2026-08-21T09:34:10.066Z
WT-26-0133 | records_pw_prw | prw-pw | 2026-08-21T09:34:13.317Z
WT-26-0134 | records_pw_prw | prw-pw | 2026-08-15T08:11:54.045Z
WP-26-0127 | records_wfi | wfi-pus | 2026-08-29T08:10:48.715Z
WP-26-0128 | records_wfi | wfi-pus | 2026-08-15T08:14:07.228Z
WT-26-0135 | records_pw_prw | prw-pw | 2026-08-17T06:17:44.764Z
WP-26-0129 | records_wfi | wfi-pus | 2026-08-29T08:10:51.738Z
WP-26-0130 | records_wfi | wfi-pus | 2026-08-20T09:14:03.330Z
WP-26-0131 | records_wfi | wfi-pus | 2026-08-20T09:14:05.850Z
WP-26-0132 | records_wfi | wfi-pus | 2026-08-29T08:10:56.083Z
WP-26-0133 | records_wfi | wfi-pus | 2026-08-21T09:46:23.386Z
WT-26-0136 | records_pw_prw | prw-pw | 2026-08-21T09:34:15.933Z
WT-26-0137 | records_pw_prw | prw-pw | 2026-08-21T09:34:19.238Z
WT-26-0138 | records_pw_prw | prw-pw | 2026-08-26T02:17:13.295Z
WT-26-0139 | records_pw_prw | prw-pw | 2026-08-26T02:17:18.180Z
WT-26-0140 | records_pw_prw | prw-pw | 2026-08-29T08:11:55.792Z
WT-26-0141 | records_pw_prw | prw-pw | 2026-08-29T08:11:59.716Z
WP-26-0134 | records_wfi | wfi-pus | 2026-09-03T02:24:14.148Z
WP-26-0135 | records_wfi | wfi-pus | 2026-08-29T08:11:01.731Z
WP-26-0136 | records_wfi | wfi-pus | 2026-08-29T08:11:04.100Z
WP-26-0137 | records_wfi | wfi-pus | 2026-09-03T02:24:19.340Z
WP-26-0138 | records_wfi | wfi-pus | 2026-08-29T08:11:09.602Z
WT-26-0142 | records_pw_prw | prw-pw | 2026-09-01T10:01:44.346Z
WT-26-0143 | records_pw_prw | prw-pw | 2026-09-01T10:01:48.176Z
WT-26-0144 | records_pw_prw | prw-pw | 2026-09-01T10:01:52.774Z
WP-26-0139 | records_wfi | wfi-pus | 2026-09-03T02:24:22.264Z
WP-26-0140 | records_wfi | wfi-pus | 2026-09-03T02:24:25.651Z
WP-26-0141 | records_wfi | wfi-pus | 2026-09-03T02:24:29.003Z

## Backup prw-pw
samplingDate | samplingPoint | samplingTag | recordStatus | worksheetCreate | noLocation | building | location | waterType | performedDate | determinedDate | result1 | result2 | resultAvg | comment | criteria | statusResult | Exclude | worksheet No. | status | syncStatus
2026-01-06 | OLD29 | DV136.05 | PQ3-Week1 | TRUE | 12-3-037 | Building 12 | GLASSWARE WASHING 1 | PW | 2026-01-07 | 2026-01-10 | 0 | 0 | 0 | NA | 100 | PASSED | FALSE | WT-26-0001 | complete | pending
2026-01-06 | OLD30 | DV136.06 | PQ3-Week1 | TRUE | 12-3-037 | Building 12 | GLASSWARE WASHING 1 | PW | 2026-01-07 | 2026-01-10 | 0 | 0 | 0 | NA | 100 | PASSED | FALSE | WT-26-0001 | complete | pending
2026-01-06 | OLD26 | DV136.10 | PQ3-Week1 | TRUE | 12-3-056 | Building 12 | MEDIA PREPARATION | PW | 2026-01-07 | 2026-01-10 | 0 | 0 | 0 | NA | 100 | PASSED | FALSE | WT-26-0001 | complete | pending
2026-01-06 | OLD24 | DV136.11 | PQ3-Week1 | TRUE | 12-3-059 | Building 12 | AUTOCLAVE | PW | 2026-01-07 | 2026-01-10 | 0 | 0 | 0 | NA | 100 | PASSED | FALSE | WT-26-0001 | complete | pending
2026-01-06 | OLD25 | DV136.12 | PQ3-Week1 | TRUE | 12-3-056 | Building 12 | MEDIA PREPARATION | PW | 2026-01-07 | 2026-01-10 | 0 | 0 | 0 | NA | 100 | PASSED | FALSE | WT-26-0001 | complete | pending
2026-01-06 | OLD22 | DV136.13 | PQ3-Week1 | TRUE | 12-3-057 | Building 12 | STERILIZATION | PW | 2026-01-07 | 2026-01-10 | 0 | 0 | 0 | NA | 100 | PASSED | FALSE | WT-26-0001 | complete | pending
2026-01-06 | OLD27 | DV136.14 | PQ3-Week1 | TRUE | 12-3-074 | Building 12 | DECONTAMINATION | PW | 2026-01-07 | 2026-01-10 | 0 | 0 | 0 | NA | 100 | PASSED | FALSE | WT-26-0001 | complete | pending
2026-01-06 | OLD21 | DV136.15 | PQ3-Week1 | TRUE | 12-3-078 | Building 12 | GLASSWARE WASHING 2 | PW | 2026-01-07 | 2026-01-10 | 0 | 0 | 0 | NA | 100 | PASSED | FALSE | WT-26-0001 | complete | pending
2026-01-06 | OLD28 | DV136.18 | PQ3-Week1 | TRUE | 12-3-037 | Building 12 | GLASSWARE WASHING 1 | PW | 2026-01-07 | 2026-01-10 | 0 | 0 | 0 | NA | 100 | PASSED | FALSE | WT-26-0001 | complete | pending
2026-01-06 | OLD23 | SV136.18 | PQ3-Week1 | TRUE | 12-3-059 | Building 12 | AUTOCLAVE | PW | 2026-01-07 | 2026-01-10 | 0 | 0 | 0 | NA | 100 | PASSED | FALSE | WT-26-0001 | complete | pending
2026-01-06 | GOLD07 | SV137.01 | PQ3-Week1 | TRUE | WATER SYSTEM (B12) | Building 12 | Return loop (B12) | PW | 2026-01-07 | 2026-01-10 | 0 | 0 | 0 | NA | 100 | PASSED | FALSE | WT-26-0001 | complete | pending
2026-01-06 | GOLD03 | V50-11C (12) | PQ3-Week1 | TRUE | WATER SYSTEM (B12) | Building 12 | After RO (Before EDI) (B12) | RO water | 2026-01-07 | 2026-01-10 | 0 | 0 | 0 | NA | 500 | PASSED | FALSE | WT-26-0001 | complete | pending
2026-01-06 | GOLD04 | V50-39 (12) | PQ3-Week1 | TRUE | WATER SYSTEM (B12) | Building 12 | After EDI (B12) | PW | 2026-01-07 | 2026-01-10 | 0 | 0 | 0 | NA | 100 | PASSED | FALSE | WT-26-0001 | complete | pending
2026-01-06 | GOLD02 | V50-61 (12) | PQ3-Week1 | TRUE | WATER SYSTEM (B12) | Building 12 | After Cartridge filter 5 µm (B12) | PRW | 2026-01-07 | 2026-01-10 | 2 | 2 | 2 | NA | 500 | PASSED | FALSE | WT-26-0001 | complete | pending
2026-01-06 | GOLD01 | VB-05 (12) | PQ3-Week1 | TRUE | WATER SYSTEM (B12) | Building 12 | After Chlorine circulation tank | PRW | 2026-01-07 | 2026-01-10 | 0 | 0 | 0 | NA | 500 | PASSED | FALSE | WT-26-0001 | complete | pending
2026-01-06 | OCL02 | DV126.01 | PQ3-Week1 | TRUE | 16-1-082 | Building 16 | WASHING | PW | 2026-01-07 | 2026-01-10 | 0 | 0 | 0 | NA | 100 | PASSED | FALSE | WT-26-0002 | complete | pending
2026-01-06 | OCL01 | DV126.02 | PQ3-Week1 | TRUE | 16-1-082 | Building 16 | WASHING | PW | 2026-01-07 | 2026-01-10 | 0 | 0 | 0 | NA | 100 | PASSED | FALSE | WT-26-0002 | complete | pending
2026-01-06 | OCL04 | DV126.03 | PQ3-Week1 | TRUE | 16-1-098 | Building 16 | CIP/SIP (SINK WASHING) | PW | 2026-01-07 | 2026-01-10 | 0 | 0 | 0 | NA | 100 | PASSED | FALSE | WT-26-0002 | complete | pending
2026-01-06 | OCL05 | SV126.01 | PQ3-Week1 | TRUE | 16-1-092 | Building 16 | LINEN WASHING | PW | 2026-01-07 | 2026-01-10 | 0 | 0 | 0 | NA | 100 | PASSED | FALSE | WT-26-0002 | complete | pending
2026-01-06 | OCL03 | SV126.02 | PQ3-Week1 | TRUE | 16-1-098 | Building 16 | CIP/SIP (EQUIPMENT REQUIREMENT – 200L) | PW | 2026-01-07 | 2026-01-10 | 0 | 0 | 0 | NA | 100 | PASSED | FALSE | WT-26-0002 | complete | pending
2026-01-06 | OCL22 | SV126.03 | PQ3-Week1 | TRUE | 16-2-010 | Building 16 | WATER SYSTEM (WFI) | PW | 2026-01-07 | 2026-01-10 | 0 | 0 | 0 | NA | 100 | PASSED | FALSE | WT-26-0002 | complete | pending
2026-01-06 | GOCL08 | SV127.01 | PQ3-Week1 | TRUE | WATER SYSTEM (B16) | Building 16 | Return loop (B16) | PW | 2026-01-07 | 2026-01-10 | 0 | 0 | 0 | NA | 100 | PASSED | FALSE | WT-26-0002 | complete | pending
2026-01-06 | GOCL03 | V50-11C (16) | PQ3-Week1 | TRUE | WATER SYSTEM (B16) | Building 16 | After RO (Before EDI) (B16) | RO water | 2026-01-07 | 2026-01-10 | 0 | 0 | 0 | NA | 500 | PASSED | FALSE | WT-26-0002 | complete | pending
2026-01-06 | GOCL04 | V50-39 (16) | PQ3-Week1 | TRUE | WATER SYSTEM (B16) | Building 16 | After EDI (B16) | PW | 2026-01-07 | 2026-01-10 | 0 | 0 | 0 | NA | 100 | PASSED | FALSE | WT-26-0002 | complete | pending
2026-01-06 | GOCL02 | V50-61 (16) | PQ3-Week1 | TRUE | WATER SYSTEM (B16) | Building 16 | After Cartridge filter 5 µm (B16) | PRW | 2026-01-07 | 2026-01-10 | 111 | 5 | 58 | NA | 500 | PASSED | FALSE | WT-26-0002 | complete | pending
2026-01-06 | GOCL01 | VB-05 (16) | PQ3-Week1 | TRUE | WATER SYSTEM (B16) | Building 16 | After Chlorine circulation tank (B16) | PRW | 2026-01-07 | 2026-01-10 | 0 | 0 | 0 | NA | 500 | PASSED | FALSE | WT-26-0002 | complete | pending
2026-01-09 | BU19-14 | SV-14 | PQ3-Week1 | TRUE | PROCESS WATER (B19) | Building 19 | AFTER RO SYSTEM NO.12 SV14 | PRW | 2026-01-10 | 2026-01-13 | 0 | 0 | 0 | NA | 500 | PASSED | FALSE | WT-26-0003 | complete | pending
2026-01-09 | OSD12 | DV116.12 | PQ3-Week1 | TRUE | 10-3-078 | Building 10 | WASHING | PW | 2026-01-10 | 2026-01-13 | 0 | 0 | 0 | NA | 100 | PASSED | FALSE | WT-26-0004 | complete | pending
2026-01-09 | OSD11 | DV116.13 | PQ3-Week1 | TRUE | 10-3-078 | Building 10 | WASHING | PW | 2026-01-10 | 2026-01-13 | 0 | 0 | 0 | NA | 100 | PASSED | FALSE | WT-26-0004 | complete | pending
2026-01-09 | OSD09 | DV116.14 | PQ3-Week1 | TRUE | 10-3-086 | Building 10 | TOOL WASHING | PW | 2026-01-10 | 2026-01-13 | 0 | 0 | 0 | NA | 100 | PASSED | FALSE | WT-26-0004 | complete | pending
2026-01-09 | OSD28 | DV116.15 | PQ3-Week1 | TRUE | 10-3-104 | Building 10 | BINDER PREPARATION | PW | 2026-01-10 | 2026-01-13 | 0 | 0 | 0 | NA | 100 | PASSED | FALSE | WT-26-0004 | complete | pending
2026-01-09 | OSD07 | DV116.16 | PQ3-Week1 | TRUE | 10-3-107 | Building 10 | WET GRANULATION-2 | PW | 2026-01-10 | 2026-01-13 | 0 | 0 | 0 | NA | 100 | PASSED | FALSE | WT-26-0004 | complete | pending
2026-01-09 | OSD27 | DV116.17 | PQ3-Week1 | TRUE | 10-3-117 | Building 10 | IPQC-2 | PW | 2026-01-10 | 2026-01-13 | 0 | 0 | 0 | NA | 100 | PASSED | FALSE | WT-26-0004 | complete | pending
2026-01-09 | OSD06 | DV116.18 | PQ3-Week1 | TRUE | 10-3-111 | Building 10 | WET GRANULATION-5 | PW | 2026-01-10 | 2026-01-13 | 0 | 0 | 0 | NA | 100 | PASSED | FALSE | WT-26-0004 | complete | pending
2026-01-09 | OSD10 | SV116.09 | PQ3-Week1 | TRUE | 10-3-078 | Building 10 | WASHING | PW | 2026-01-10 | 2026-01-13 | 0 | 0 | 0 | NA | 100 | PASSED | FALSE | WT-26-0004 | complete | pending
2026-01-09 | OSD08 | SV116.11 | PQ3-Week1 | TRUE | 10-3-107 | Building 10 | WET GRANULATION-2 | PW | 2026-01-10 | 2026-01-13 | 0 | 0 | 0 | NA | 100 | PASSED | FALSE | WT-26-0004 | complete | pending
2026-01-09 | GOSD08 | SV117.01 | PQ3-Week1 | TRUE | WATER SYSTEM (B10) | Building 10 | Return loop (B10) | PW | 2026-01-10 | 2026-01-13 | 0 | 0 | 0 | NA | 100 | PASSED | FALSE | WT-26-0004 | complete | pending
2026-01-09 | GOSD04 | V50-11C(10) | PQ3-Week1 | TRUE | WATER SYSTEM (B10) | Building 10 | After RO (Before EDI) (B10) | RO water | 2026-01-10 | 2026-01-13 | 0 | 0 | 0 | NA | 500 | PASSED | FALSE | WT-26-0004 | complete | pending
2026-01-09 | GOSD05 | V50-39(10) | PQ3-Week1 | TRUE | WATER SYSTEM (B10) | Building 10 | After EDI (B10) | PW | 2026-01-10 | 2026-01-13 | 0 | 0 | 0 | NA | 100 | PASSED | FALSE | WT-26-0004 | complete | pending
2026-01-09 | GOSD03 | V50-61(10) | PQ3-Week1 | TRUE | WATER SYSTEM (B10) | Building 10 | After Cartridge filter 5 µm (B10) | PRW | 2026-01-10 | 2026-01-13 | 0 | 0 | 0 | NA | 500 | PASSED | FALSE | WT-26-0004 | complete | pending
2026-01-09 | GOSD01 | VB-05(10) | PQ3-Week1 | TRUE | WATER SYSTEM (B10) | Building 10 | After Chlorine circulation tank (B10) | PRW | 2026-01-10 | 2026-01-13 | 0 | 0 | 0 | NA | 500 | PASSED | FALSE | WT-26-0004 | complete | pending
2026-01-13 | OCL21 | DV126.05 | PQ3-Week2 | TRUE | 16-3-054 | Building 16 | WASHING | PW | 2026-01-14 | 2026-01-17 | 0 | 0 | 0 | NA | 100 | PASSED | FALSE | WT-26-0005 | complete | pending
2026-01-13 | OCL14 | DV126.11 | PQ3-Week2 | TRUE | 16-3-073 | Building 16 | MFG 4 (5000L) | PW | 2026-01-14 | 2026-01-17 | 0 | 0 | 0 | NA | 100 | PASSED | FALSE | WT-26-0005 | complete | pending
2026-01-13 | GOCL05 | SV123.01 | PQ3-Week2 | TRUE | WATER SYSTEM (B16) | Building 16 | After Storage tank (B16) | PW | 2026-01-14 | 2026-01-17 | 0 | 0 | 0 | NA | 100 | PASSED | FALSE | WT-26-0005 | complete | pending
2026-01-13 | GOCL07 | SV125.02 | PQ3-Week2 | TRUE | WATER SYSTEM (B16) | Building 16 | After UV (B16) | PW | 2026-01-14 | 2026-01-17 | 0 | 0 | 0 | NA | 100 | PASSED | FALSE | WT-26-0005 | complete | pending
2026-01-13 | OCL23 | SV126.04 | PQ3-Week2 | TRUE | 16-2-010 | Building 16 | WATER SYSTEM (PSG) | PW | 2026-01-14 | 2026-01-17 | 0 | 0 | 0 | NA | 100 | PASSED | FALSE | WT-26-0005 | complete | pending
2026-01-13 | OCL15 | SV126.14 | PQ3-Week2 | TRUE | 16-3-073 | Building 16 | MFG 4 (400L) | PW | 2026-01-14 | 2026-01-17 | 0 | 0 | 0 | NA | 100 | PASSED | FALSE | WT-26-0005 | complete | pending
2026-01-13 | OCL17 | SV126.15 | PQ3-Week2 | TRUE | 16-3-075 | Building 16 | MFG 5 PROCESS (2000L) | PW | 2026-01-14 | 2026-01-17 | 0 | 0 | 0 | NA | 100 | PASSED | FALSE | WT-26-0005 | complete | pending
2026-01-13 | OCL13 | SV126.19 | PQ3-Week2 | TRUE | 16-3-087 | Building 16 | CIP 2 (EQUIPMENT REQUIREMENT) | PW | 2026-01-14 | 2026-01-17 | 0 | 0 | 0 | NA | 100 | PASSED | FALSE | WT-26-0005 | complete | pending
2026-01-13 | GOCL08 | SV127.01 | PQ3-Week2 | TRUE | WATER SYSTEM (B16) | Building 16 | Return loop (B16) | PW | 2026-01-14 | 2026-01-17 | 0 | 0 | 0 | NA | 100 | PASSED | FALSE | WT-26-0005 | complete | pending
2026-01-13 | OLD15 | DV136.02 | PQ3-Week2 | TRUE | 12-2-028 | Building 12 | ALCOHOL STORAGE | PW | 2026-01-14 | 2026-01-17 | 0 | 0 | 0 | NA | 100 | PASSED | FALSE | WT-26-0006 | complete | pending
2026-01-13 | OLD31 | DV136.07 | PQ3-Week2 | TRUE | 12-3-039 | Building 12 | INSTRUMENT 7 | PW | 2026-01-14 | 2026-01-17 | 0 | 0 | 0 | NA | 100 | PASSED | FALSE | WT-26-0006 | complete | pending
2026-01-13 | GOLD05 | SV133.01 | PQ3-Week2 | TRUE | WATER SYSTEM (B12) | Building 12 | After Storage tank (B12) | PW | 2026-01-14 | 2026-01-17 | 0 | 0 | 0 | NA | 100 | PASSED | FALSE | WT-26-0006 | complete | pending
2026-01-13 | GOLD06 | SV135.02 | PQ3-Week2 | TRUE | WATER SYSTEM (B12) | Building 12 | After UV (B12) | PW | 2026-01-14 | 2026-01-17 | 0 | 0 | 0 | NA | 100 | PASSED | FALSE | WT-26-0006 | complete | pending
2026-01-13 | OLD12 | SV136.03 | PQ3-Week2 | TRUE | 12-2-032 | Building 12 | CAMPHORATED OPIUM TINCTURE | PW | 2026-01-14 | 2026-01-17 | 0 | 0 | 0 | NA | 100 | PASSED | FALSE | WT-26-0006 | complete | pending
2026-01-13 | OLD14 | SV136.04 | PQ3-Week2 | TRUE | 12-2-030 | Building 12 | OPIUM TINCTURE | PW | 2026-01-14 | 2026-01-17 | 0 | 0 | 0 | NA | 100 | PASSED | FALSE | WT-26-0006 | complete | pending
2026-01-13 | OLD13 | SV136.05 | PQ3-Week2 | TRUE | 12-2-032 | Building 12 | CAMPHORATED OPIUM TINCTURE | PW | 2026-01-14 | 2026-01-17 | 0 | 0 | 0 | NA | 100 | PASSED | FALSE | WT-26-0006 | complete | pending
2026-01-13 | OLD05 | SV136.06 | PQ3-Week2 | TRUE | 12-2-034 | Building 12 | SYRUP PREPARATION | PW | 2026-01-14 | 2026-01-17 | 0 | 0 | 0 | NA | 100 | PASSED | FALSE | WT-26-0006 | complete | pending
2026-01-13 | OLD04 | SV136.07 | PQ3-Week2 | TRUE | 12-2-034 | Building 12 | SYRUP PREPARATION | PW | 2026-01-14 | 2026-01-17 | 0 | 0 | 0 | NA | 100 | PASSED | FALSE | WT-26-0006 | complete | pending
2026-01-13 | OLD03 | SV136.12 | PQ3-Week2 | TRUE | 12-2-036 | Building 12 | CIP 1 | PW | 2026-01-14 | 2026-01-17 | 0 | 0 | 0 | NA | 100 | PASSED | FALSE | WT-26-0006 | complete | pending
2026-01-13 | GOLD07 | SV137.01 | PQ3-Week2 | TRUE | WATER SYSTEM (B12) | Building 12 | Return loop (B12) | PW | 2026-01-14 | 2026-01-17 | 0 | 0 | 0 | NA | 100 | PASSED | FALSE | WT-26-0006 | complete | pending
2026-01-16 | OSD36 | DV116.03 | PQ3-Week2 | TRUE | 10-2-034 | Building 10 | SAMPLE PREPARATION | PW | 2026-01-17 | 2026-01-20 | 0 | 0 | 0 | NA | 100 | PASSED | FALSE | WT-26-0007 | complete | pending
2026-01-16 | OSD40 | DV116.04 | PQ3-Week2 | TRUE | 10-2-037 | Building 10 | SKID FOR BIN WASHING-1 | PW | 2026-01-17 | 2026-01-20 | 0 | 0 | 0 | NA | 100 | PASSED | FALSE | WT-26-0007 | complete | pending
2026-01-16 | OSD39 | DV116.05 | PQ3-Week2 | TRUE | 10-2-032 | Building 10 | GLASS-WARE WASHING | PW | 2026-01-17 | 2026-01-20 | 0 | 0 | 0 | NA | 100 | PASSED | FALSE | WT-26-0007 | complete | pending
2026-01-16 | OSD37 | DV116.06 | PQ3-Week2 | TRUE | 10-2-034 | Building 10 | SAMPLE PREPARATION | PW | 2026-01-17 | 2026-01-20 | 0 | 0 | 0 | NA | 100 | PASSED | FALSE | WT-26-0007 | complete | pending
2026-01-16 | OSD38 | DV116.07 | PQ3-Week2 | TRUE | 10-2-032 | Building 10 | GLASS-WARE WASHING | PW | 2026-01-17 | 2026-01-20 | 0 | 0 | 0 | NA | 100 | PASSED | FALSE | WT-26-0007 | complete | pending
2026-01-16 | OSD25 | DV116.08 | PQ3-Week2 | TRUE | 10-3-059 | Building 10 | COATING SOLUTION PREP.-1 | PW | 2026-01-17 | 2026-01-20 | 0 | 0 | 0 | NA | 100 | PASSED | FALSE | WT-26-0007 | complete | pending
2026-01-16 | OSD24 | DV116.09 | PQ3-Week2 | TRUE | 10-3-060 | Building 10 | COATING SOLUTION PREP.-2 | PW | 2026-01-17 | 2026-01-20 | 0 | 0 | 0 | NA | 100 | PASSED | FALSE | WT-26-0007 | complete | pending
2026-01-16 | OSD31 | DV116.10 | PQ3-Week2 | TRUE | 10-3-065 | Building 10 | COATING SOLUTION PREP.-3 | PW | 2026-01-17 | 2026-01-20 | 0 | 0 | 0 | NA | 100 | PASSED | FALSE | WT-26-0007 | complete | pending
2026-01-16 | OSD30 | DV116.11 | PQ3-Week2 | TRUE | 10-3-066 | Building 10 | COATING SOLUTION PREP.-4 | PW | 2026-01-17 | 2026-01-20 | 0 | 0 | 0 | NA | 100 | PASSED | FALSE | WT-26-0007 | complete | pending
2026-01-16 | GOSD06 | SV113.01 | PQ3-Week2 | TRUE | WATER SYSTEM (B10) | Building 10 | After Storage tank (B10) | PW | 2026-01-17 | 2026-01-20 | 0 | 0 | 0 | NA | 100 | PASSED | FALSE | WT-26-0007 | complete | pending
2026-01-16 | GOSD07 | SV115.02 | PQ3-Week2 | TRUE | WATER SYSTEM (B10) | Building 10 | After UV (B10) | PW | 2026-01-17 | 2026-01-20 | 0 | 0 | 0 | NA | 100 | PASSED | FALSE | WT-26-0007 | complete | pending
2026-01-16 | OSD26 | SV116.03 | PQ3-Week2 | TRUE | 10-3-058 | Building 10 | COATING ROOM-1 | PW | 2026-01-17 | 2026-01-20 | 0 | 0 | 0 | NA | 100 | PASSED | FALSE | WT-26-0007 | complete | pending
2026-01-16 | OSD23 | SV116.04 | PQ3-Week2 | TRUE | 10-3-061 | Building 10 | COATING ROOM-2 | PW | 2026-01-17 | 2026-01-20 | 0 | 0 | 0 | NA | 100 | PASSED | FALSE | WT-26-0007 | complete | pending
2026-01-16 | OSD22 | SV116.05 | PQ3-Week2 | TRUE | 10-3-062 | Building 10 | COATING ROOM-3 | PW | 2026-01-17 | 2026-01-20 | 0 | 0 | 0 | NA | 100 | PASSED | FALSE | WT-26-0007 | complete | pending
2026-01-16 | OSD33 | SV116.06 | PQ3-Week2 | TRUE | 10-3-063 | Building 10 | COATING ROOM-4 | PW | 2026-01-17 | 2026-01-20 | 0 | 0 | 0 | NA | 100 | PASSED | FALSE | WT-26-0007 | complete | pending
2026-01-16 | OSD32 | SV116.07 | PQ3-Week2 | TRUE | 10-3-064 | Building 10 | COATING ROOM-5 | PW | 2026-01-17 | 2026-01-20 | 0 | 0 | 0 | NA | 100 | PASSED | FALSE | WT-26-0007 | complete | pending
2026-01-16 | OSD29 | SV116.08 | PQ3-Week2 | TRUE | 10-3-067 | Building 10 | COATING ROOM-6 | PW | 2026-01-17 | 2026-01-20 | 0 | 0 | 0 | NA | 100 | PASSED | FALSE | WT-26-0007 | complete | pending
2026-01-16 | GOSD08 | SV117.01 | PQ3-Week2 | TRUE | WATER SYSTEM (B10) | Building 10 | Return loop (B10) | PW | 2026-01-17 | 2026-01-20 | 0 | 0 | 0 | NA | 100 | PASSED | FALSE | WT-26-0007 | complete | pending
2026-01-20 | OLD19 | DV136.01 | PQ3-Week3 | TRUE | 12-1-035 | Building 12 | SUGAR TRANSFERRING | PW | 2026-01-21 | 2026-01-24 | 0 | 0 | 0 | NA | 100 | PASSED | FALSE | WT-26-0009 | complete | pending
2026-01-20 | OLD17 | DV136.03 | PQ3-Week3 | TRUE | 12-2-053 | Building 12 | IPQC | PW | 2026-01-21 | 2026-01-24 | 0 | 0 | 0 | NA | 100 | PASSED | FALSE | WT-26-0009 | complete | pending
2026-01-20 | OLD34 | DV136.04 | PQ3-Week3 | TRUE | 12-2-077 | Building 12 | WATER SYSTEM ROOM | PW | 2026-01-21 | 2026-01-24 | 0 | 0 | 0 | NA | 100 | PASSED | FALSE | WT-26-0009 | complete | pending
2026-01-20 | OLD20 | DV136.16 | PQ3-Week3 | TRUE | 12-1-064 | Building 12 | WASHING | PW | 2026-01-21 | 2026-01-24 | 0 | 0 | 0 | NA | 100 | PASSED | FALSE | WT-26-0009 | complete | pending
2026-01-20 | OLD01 | DV136.17 | PQ3-Week3 | TRUE | 12-2-065 | Building 12 | WASHING | PW | 2026-01-21 | 2026-01-24 | 0 | 0 | 0 | NA | 100 | PASSED | FALSE | WT-26-0009 | complete | pending
2026-01-20 | OLD10 | SV136.15 | PQ3-Week3 | TRUE | 12-2-055 | Building 12 | CIP 3 | PW | 2026-01-21 | 2026-01-24 | 0 | 0 | 0 | NA | 100 | PASSED | FALSE | WT-26-0009 | complete | pending
2026-01-20 | OLD02 | SV136.16 | PQ3-Week3 | TRUE | 12-2-057 | Building 12 | CIP 2 | PW | 2026-01-21 | 2026-01-24 | 0 | 0 | 0 | NA | 100 | PASSED | FALSE | WT-26-0009 | complete | pending
2026-01-20 | GOLD07 | SV137.01 | PQ3-Week3 | TRUE | WATER SYSTEM (B12) | Building 12 | Return loop (B12) | PW | 2026-01-21 | 2026-01-24 | 0 | 0 | 0 | NA | 100 | PASSED | FALSE | WT-26-0009 | complete | pending
2026-01-20 | GOLD03 | V50-11C (12) | PQ3-Week3 | TRUE | WATER SYSTEM (B12) | Building 12 | After RO (Before EDI) (B12) | RO water | 2026-01-21 | 2026-01-24 | 0 | 0 | 0 | NA | 500 | PASSED | FALSE | WT-26-0009 | complete | pending
2026-01-20 | GOLD04 | V50-39 (12) | PQ3-Week3 | TRUE | WATER SYSTEM (B12) | Building 12 | After EDI (B12) | PW | 2026-01-21 | 2026-01-24 | 0 | 0 | 0 | NA | 100 | PASSED | FALSE | WT-26-0009 | complete | pending
2026-01-20 | GOLD02 | V50-61 (12) | PQ3-Week3 | TRUE | WATER SYSTEM (B12) | Building 12 | After Cartridge filter 5 µm (B12) | PRW | 2026-01-21 | 2026-01-24 | 0 | 0 | 0 | NA | 500 | PASSED | FALSE | WT-26-0009 | complete | pending
2026-01-20 | GOLD01 | VB-05 (12) | PQ3-Week3 | TRUE | WATER SYSTEM (B12) | Building 12 | After Chlorine circulation tank | PRW | 2026-01-21 | 2026-01-23 | 0 | 0 | 0 | NA | 500 | PASSED | FALSE | WT-26-0009 | complete | pending
2026-01-20 | OCL24 | DV126.04 | PQ3-Week3 | TRUE | 16-2-010 | Building 16 | WATER SYSTEM (PW) | PW | 2026-01-21 | 2026-01-24 | 0 | 0 | 0 | NA | 100 | PASSED | FALSE | WT-26-0010 | complete | pending
2026-01-20 | OCL08 | DV126.09 | PQ3-Week3 | TRUE | 16-3-090 | Building 16 | CIP 1 (ZINK WASHING) | PW | 2026-01-21 | 2026-01-24 | 0 | 0 | 0 | NA | 100 | PASSED | FALSE | WT-26-0010 | complete | pending
2026-01-20 | OCL20 | SV126.05 | PQ3-Week3 | TRUE | 16-3-049 | Building 16 | LINEN WASHING | PW | 2026-01-21 | 2026-01-24 | 0 | 0 | 0 | NA | 100 | PASSED | FALSE | WT-26-0010 | complete | pending
2026-01-20 | OCL06 | SV126.06 | PQ3-Week3 | TRUE | 16-3-067 | Building 16 | MFG 1 | PW | 2026-01-21 | 2026-01-24 | 0 | 0 | 0 | NA | 100 | PASSED | FALSE | WT-26-0010 | complete | pending
2026-01-20 | OCL16 | SV126.18 | PQ3-Week3 | TRUE | 16-3-085 | Building 16 | CIP 3 (EQUIPMENT REQUIREMENT) | PW | 2026-01-21 | 2026-01-24 | 0 | 0 | 0 | NA | 100 | PASSED | FALSE | WT-26-0010 | complete | pending
2026-01-20 | OCL07 | SV126.21 | PQ3-Week3 | TRUE | 16-3-090 | Building 16 | CIP 1 (EQUIPMENT REQUIREMENT) | PW | 2026-01-21 | 2026-01-24 | 0 | 0 | 0 | NA | 100 | PASSED | FALSE | WT-26-0010 | complete | pending
2026-01-20 | GOCL08 | SV127.01 | PQ3-Week3 | TRUE | WATER SYSTEM (B16) | Building 16 | Return loop (B16) | PW | 2026-01-21 | 2026-01-24 | 0 | 0 | 0 | NA | 100 | PASSED | FALSE | WT-26-0010 | complete | pending
2026-01-20 | GOCL03 | V50-11C (16) | PQ3-Week3 | TRUE | WATER SYSTEM (B16) | Building 16 | After RO (Before EDI) (B16) | RO water | 2026-01-21 | 2026-01-24 | 0 | 0 | 0 | NA | 500 | PASSED | FALSE | WT-26-0010 | complete | pending
2026-01-20 | GOCL04 | V50-39 (16) | PQ3-Week3 | TRUE | WATER SYSTEM (B16) | Building 16 | After EDI (B16) | PW | 2026-01-21 | 2026-01-24 | 0 | 0 | 0 | NA | 100 | PASSED | FALSE | WT-26-0010 | complete | pending
2026-01-20 | GOCL02 | V50-61 (16) | PQ3-Week3 | TRUE | WATER SYSTEM (B16) | Building 16 | After Cartridge filter 5 µm (B16) | PRW | 2026-01-21 | 2026-01-24 | 2 | 2 | 2 | NA | 500 | PASSED | FALSE | WT-26-0010 | complete | pending
2026-01-20 | GOCL01 | VB-05 (16) | PQ3-Week3 | TRUE | WATER SYSTEM (B16) | Building 16 | After Chlorine circulation tank (B16) | PRW | 2026-01-21 | 2026-01-24 | 0 | 0 | 0 | NA | 500 | PASSED | FALSE | WT-26-0010 | complete | pending
2026-01-22 | OSD42 | DV116.01 | PQ3-Week3 | TRUE | 10-1-057 | Building 10 | WASHING-P | PW | 2026-01-23 | 2026-01-26 | 0 | 0 | 0 | NA | 100 | PASSED | FALSE | WT-26-0011 | complete | pending
2026-01-22 | OSD41 | DV116.02 | PQ3-Week3 | TRUE | 10-1-115 | Building 10 | WASHING | PW | 2026-01-23 | 2026-01-26 | 0 | 0 | 0 | NA | 100 | PASSED | FALSE | WT-26-0011 | complete | pending
2026-01-22 | OSD20 | DV116.19 | PQ3-Week3 | TRUE | 10-3-143 | Building 10 | COATING SOLUTION PREP.-P | PW | 2026-01-23 | 2026-01-26 | 0 | 0 | 0 | NA | 100 | PASSED | FALSE | WT-26-0011 | complete | pending
2026-01-22 | OSD19 | DV116.20 | PQ3-Week3 | TRUE | 10-3-149 | Building 10 | IPQC-1-P | PW | 2026-01-23 | 2026-01-26 | 0 | 0 | 0 | NA | 100 | PASSED | FALSE | WT-26-0011 | complete | pending
2026-01-22 | OSD16 | DV116.21 | PQ3-Week3 | TRUE | 10-3-152 | Building 10 | WASHING-P | PW | 2026-01-23 | 2026-01-26 | 0 | 0 | 0 | NA | 100 | PASSED | FALSE | WT-26-0011 | complete | pending
2026-01-22 | OSD17 | DV116.22 | PQ3-Week3 | TRUE | 10-3-152 | Building 10 | WASHING-P | PW | 2026-01-23 | 2026-01-26 | 0 | 0 | 0 | NA | 100 | PASSED | FALSE | WT-26-0011 | complete | pending
2026-01-22 | OSD15 | DV116.23 | PQ3-Week3 | TRUE | 10-3-159 | Building 10 | BINDER PREPARATION-P | PW | 2026-01-23 | 2026-01-26 | 0 | 0 | 0 | NA | 100 | PASSED | FALSE | WT-26-0011 | complete | pending
2026-01-22 | OSD14 | DV116.24 | PQ3-Week3 | TRUE | 10-3-163 | Building 10 | WET GRANULATION 1-P | PW | 2026-01-23 | 2026-01-26 | 0 | 0 | 0 | NA | 100 | PASSED | FALSE | WT-26-0011 | complete | pending
2026-01-22 | OSD13 | DV116.25 | PQ3-Week3 | TRUE | 10-3-171 | Building 10 | TOOL WASHING-P | PW | 2026-01-23 | 2026-01-26 | 0 | 0 | 0 | NA | 100 | PASSED | FALSE | WT-26-0011 | complete | pending
2026-01-22 | OSD21 | SV116.12 | PQ3-Week3 | TRUE | 10-3-144 | Building 10 | COATING-P | PW | 2026-01-23 | 2026-01-26 | 0 | 0 | 0 | NA | 100 | PASSED | FALSE | WT-26-0011 | complete | pending
2026-01-22 | OSD18 | SV116.13 | PQ3-Week3 | TRUE | 10-3-152 | Building 10 | WASHING-P | PW | 2026-01-23 | 2026-01-26 | 0 | 0 | 0 | NA | 100 | PASSED | FALSE | WT-26-0011 | complete | pending
2026-01-22 | GOSD08 | SV117.01 | PQ3-Week3 | TRUE | WATER SYSTEM (B10) | Building 10 | Return loop (B10) | PW | 2026-01-23 | 2026-01-26 | 0 | 0 | 0 | NA | 100 | PASSED | FALSE | WT-26-0011 | complete | pending
2026-01-22 | GOSD04 | V50-11C(10) | PQ3-Week3 | TRUE | WATER SYSTEM (B10) | Building 10 | After RO (Before EDI) (B10) | RO water | 2026-01-23 | 2026-01-26 | 0 | 0 | 0 | NA | 500 | PASSED | FALSE | WT-26-0011 | complete | pending
2026-01-22 | GOSD02 | V50-60(10) | PQ3-Week3 | TRUE | WATER SYSTEM (B10) | Building 10 | Before Cartridge filter 5 µm (B10) | PRW | 2026-01-23 | 2026-01-26 | 0 | 0 | 0 | NA | 500 | PASSED | FALSE | WT-26-0011 | complete | pending
2026-01-22 | GOSD03 | V50-61(10) | PQ3-Week3 | TRUE | WATER SYSTEM (B10) | Building 10 | After Cartridge filter 5 µm (B10) | PRW | 2026-01-23 | 2026-01-26 | 0 | 0 | 0 | NA | 500 | PASSED | FALSE | WT-26-0011 | complete | pending
2026-01-22 | GOSD01 | VB-05(10) | PQ3-Week3 | TRUE | WATER SYSTEM (B10) | Building 10 | After Chlorine circulation tank (B10) | PRW | 2026-01-23 | 2026-01-26 | 0 | 0 | 0 | NA | 500 | PASSED | FALSE | WT-26-0011 | complete | pending
2026-01-22 | BU19-14 | SV-14 | PQ3-Week3 | TRUE | PROCESS WATER (B19) | Building 19 | AFTER RO SYSTEM NO.12 SV14 | PRW | 2026-01-23 | 2026-01-26 | 0 | 0 | 0 | NA | 500 | PASSED | FALSE | WT-26-0012 | complete | pending
2026-01-27 | OLD32 | DV136.08 | PQ3-Week4 | TRUE | 12-3-042 | Building 12 | SAMPLE PREPARATION | PW | 2026-01-28 | 2026-02-02 | 0 | 0 | 0 | NA | 100 | PASSED | FALSE | WT-26-0013 | complete | pending
2026-01-27 | OLD33 | DV136.09 | PQ3-Week4 | TRUE | 12-3-042 | Building 12 | SAMPLE PREPARATION | PW | 2026-01-28 | 2026-02-02 | 0 | 0 | 0 | NA | 100 | PASSED | FALSE | WT-26-0013 | complete | pending
2026-01-27 | GOLD05 | SV133.01 | PQ3-Week4 | TRUE | WATER SYSTEM (B12) | Building 12 | After Storage tank (B12) | PW | 2026-01-28 | 2026-02-02 | 0 | 0 | 0 | NA | 100 | PASSED | FALSE | WT-26-0013 | complete | pending
2026-01-27 | GOLD06 | SV135.02 | PQ3-Week4 | TRUE | WATER SYSTEM (B12) | Building 12 | After UV (B12) | PW | 2026-01-28 | 2026-02-02 | 0 | 0 | 0 | NA | 100 | PASSED | FALSE | WT-26-0013 | complete | pending
2026-01-27 | OLD18 | SV136.02 | PQ3-Week4 | TRUE | 12-2-024 | Building 12 | LIQUORICE EXTRACT | PW | 2026-01-28 | 2026-02-02 | 0 | 0 | 0 | NA | 100 | PASSED | FALSE | WT-26-0013 | complete | pending
2026-01-27 | OLD11 | SV136.08 | PQ3-Week4 | TRUE | 12-2-043 | Building 12 | MFG 3 | PW | 2026-01-28 | 2026-02-02 | 0 | 0 | 0 | NA | 100 | PASSED | FALSE | WT-26-0013 | complete | pending
2026-01-27 | OLD06 | SV136.09 | PQ3-Week4 | TRUE | 12-2-039 | Building 12 | MFG 1 | PW | 2026-01-28 | 2026-02-02 | 0 | 0 | 0 | NA | 100 | PASSED | FALSE | WT-26-0013 | complete | pending
2026-01-27 | OLD07 | SV136.10 | PQ3-Week4 | TRUE | 12-2-041 | Building 12 | MFG 2 | PW | 2026-01-28 | 2026-02-02 | 0 | 0 | 0 | NA | 100 | PASSED | FALSE | WT-26-0013 | complete | pending
2026-01-27 | OLD08 | SV136.11 | PQ3-Week4 | TRUE | 12-2-043 | Building 12 | MFG 3 | PW | 2026-01-28 | 2026-02-02 | 0 | 0 | 0 | NA | 100 | PASSED | FALSE | WT-26-0013 | complete | pending
2026-01-27 | OLD09 | SV136.13 | PQ3-Week4 | TRUE | 12-2-043 | Building 12 | MFG 3 | PW | 2026-01-28 | 2026-02-02 | 0 | 0 | 0 | NA | 100 | PASSED | FALSE | WT-26-0013 | complete | pending
2026-01-27 | OLD16 | SV136.14 | PQ3-Week4 | TRUE | 12-2-045 | Building 12 | MFG 4 | PW | 2026-01-28 | 2026-02-02 | 0 | 0 | 0 | NA | 100 | PASSED | FALSE | WT-26-0013 | complete | pending
2026-01-27 | GOLD07 | SV137.01 | PQ3-Week4 | TRUE | WATER SYSTEM (B12) | Building 12 | Return loop (B12) | PW | 2026-01-28 | 2026-02-02 | 0 | 0 | 0 | NA | 100 | PASSED | FALSE | WT-26-0013 | complete | pending
2026-01-27 | OCL10 | DV126.06 | PQ3-Week4 | TRUE | 16-3-069 | Building 16 | MFG 2 | PW | 2026-01-28 | 2026-02-02 | 0 | 0 | 0 | NA | 100 | PASSED | FALSE | WT-26-0014 | complete | pending
2026-01-27 | OCL19 | DV126.07 | PQ3-Week4 | TRUE | 16-3-077 | Building 16 | MFG 6 | PW | 2026-01-28 | 2026-02-02 | 0 | 0 | 0 | NA | 100 | PASSED | FALSE | WT-26-0014 | complete | pending
2026-01-27 | OCL18 | DV126.08 | PQ3-Week4 | TRUE | 16-3-077 | Building 16 | MFG 6 | PW | 2026-01-28 | 2026-02-02 | 0 | 0 | 0 | NA | 100 | PASSED | FALSE | WT-26-0014 | complete | pending
2026-01-27 | OCL09 | DV126.10 | PQ3-Week4 | TRUE | 16-3-069 | Building 16 | MFG 2 | PW | 2026-01-28 | 2026-02-02 | 1 | 0 | 1 | NA | 100 | PASSED | FALSE | WT-26-0014 | complete | pending
2026-01-27 | GOCL05 | SV123.01 | PQ3-Week4 | TRUE | WATER SYSTEM (B16) | Building 16 | After Storage tank (B16) | PW | 2026-01-28 | 2026-02-02 | 0 | 0 | 0 | NA | 100 | PASSED | FALSE | WT-26-0014 | complete | pending
2026-01-27 | GOCL07 | SV125.02 | PQ3-Week4 | TRUE | WATER SYSTEM (B16) | Building 16 | After UV (B16) | PW | 2026-01-28 | 2026-02-02 | 0 | 0 | 0 | NA | 100 | PASSED | FALSE | WT-26-0014 | complete | pending
2026-01-27 | OCL12 | SV126.09 | PQ3-Week4 | TRUE | 16-3-071 | Building 16 | MFG 3 (5000L) | PW | 2026-01-28 | 2026-02-02 | 0 | 0 | 0 | NA | 100 | PASSED | FALSE | WT-26-0014 | complete | pending
2026-01-27 | OCL11 | SV126.10 | PQ3-Week4 | TRUE | 16-3-071 | Building 16 | MFG 3 (1200L) | PW | 2026-01-28 | 2026-02-02 | 0 | 0 | 0 | NA | 100 | PASSED | FALSE | WT-26-0014 | complete | pending
2026-01-27 | GOCL08 | SV127.01 | PQ3-Week4 | TRUE | WATER SYSTEM (B16) | Building 16 | Return loop (B16) | PW | 2026-01-28 | 2026-02-02 | 0 | 0 | 0 | NA | 100 | PASSED | FALSE | WT-26-0014 | complete | pending
2026-01-28 | OSD43 | DV116.26 | PQ3-Week4 | TRUE | 10-4-015 | Building 10 | WATER SYSTEM ROOM | PW | 2026-01-29 | 2026-02-02 | 0 | 0 | 0 | NA | 100 | PASSED | FALSE | WT-26-0015 | complete | pending
2026-01-28 | GOSD06 | SV113.01 | PQ3-Week4 | TRUE | WATER SYSTEM (B10) | Building 10 | After Storage tank (B10) | PW | 2026-01-29 | 2026-02-02 | 0 | 0 | 0 | NA | 100 | PASSED | FALSE | WT-26-0015 | complete | pending
2026-01-28 | GOSD07 | SV115.02 | PQ3-Week4 | TRUE | WATER SYSTEM (B10) | Building 10 | After UV (B10) | PW | 2026-01-29 | 2026-02-02 | 0 | 0 | 0 | NA | 100 | PASSED | FALSE | WT-26-0015 | complete | pending
2026-01-28 | OSD35 | SV116.01 | PQ3-Week4 | TRUE | 10-2-021 | Building 10 | INSTRUMENT-1 | PW | 2026-01-29 | 2026-02-02 | 0 | 0 | 0 | NA | 100 | PASSED | FALSE | WT-26-0015 | complete | pending
2026-01-28 | OSD34 | SV116.02 | PQ3-Week4 | TRUE | 10-2-037 | Building 10 | SKID FOR BIN WASHING-2 | PW | 2026-01-29 | 2026-02-02 | 0 | 0 | 0 | NA | 100 | PASSED | FALSE | WT-26-0015 | complete | pending
2026-01-28 | OSD01 | SV116.15 | PQ3-Week4 | TRUE | 10-4-012 | Building 10 | CIP SKID-1 FOR BIN WASHING-1 | PW | 2026-01-29 | 2026-02-02 | 0 | 0 | 0 | NA | 100 | PASSED | FALSE | WT-26-0015 | complete | pending
2026-01-28 | OSD02 | SV116.16 | PQ3-Week4 | TRUE | 10-4-012 | Building 10 | WIP SKID-3 FOR GRANULATION POTENT | PW | 2026-01-29 | 2026-02-02 | 0 | 0 | 0 | NA | 100 | PASSED | FALSE | WT-26-0015 | complete | pending
2026-01-28 | OSD03 | SV116.17 | PQ3-Week4 | TRUE | 10-4-012 | Building 10 | CIP SKID-2 FOR BIN WASHING-1 | PW | 2026-01-29 | 2026-02-02 | 0 | 0 | 0 | NA | 100 | PASSED | FALSE | WT-26-0015 | complete | pending
2026-01-28 | OSD04 | SV116.18 | PQ3-Week4 | TRUE | 10-4-012 | Building 10 | WIP SKID-1 FOR GRANULATION NON POTENT | PW | 2026-01-29 | 2026-02-02 | 0 | 0 | 0 | NA | 100 | PASSED | FALSE | WT-26-0015 | complete | pending
2026-01-28 | OSD05 | SV116.19 | PQ3-Week4 | TRUE | 10-4-012 | Building 10 | WIP SKID-2 FOR GRANULATION NON POTENT | PW | 2026-01-29 | 2026-02-02 | 0 | 0 | 0 | NA | 100 | PASSED | FALSE | WT-26-0015 | complete | pending
2026-01-28 | GOSD08 | SV117.01 | PQ3-Week4 | TRUE | WATER SYSTEM (B10) | Building 10 | Return loop (B10) | PW | 2026-01-29 | 2026-02-02 | 0 | 0 | 0 | NA | 100 | PASSED | FALSE | WT-26-0015 | complete | pending
2026-02-03 | OCL02 | DV126.01 | PQ3-Week1 | TRUE | 16-1-082 | Building 16 | WASHING | PW | 2026-02-04 | 2026-02-07 | 0 | 0 | 0 | NA | 100 | PASSED | FALSE | WT-26-0016 | complete | pending
2026-02-03 | OCL01 | DV126.02 | PQ3-Week1 | TRUE | 16-1-082 | Building 16 | WASHING | PW | 2026-02-04 | 2026-02-07 | 0 | 0 | 0 | NA | 100 | PASSED | FALSE | WT-26-0016 | complete | pending
2026-02-03 | OCL04 | DV126.03 | PQ3-Week1 | TRUE | 16-1-098 | Building 16 | CIP/SIP (SINK WASHING) | PW | 2026-02-04 | 2026-02-07 | 0 | 0 | 0 | NA | 100 | PASSED | FALSE | WT-26-0016 | complete | pending
2026-02-03 | OCL05 | SV126.01 | PQ3-Week1 | TRUE | 16-1-092 | Building 16 | LINEN WASHING | PW | 2026-02-04 | 2026-02-07 | 0 | 0 | 0 | NA | 100 | PASSED | FALSE | WT-26-0016 | complete | pending
2026-02-03 | OCL03 | SV126.02 | PQ3-Week1 | TRUE | 16-1-098 | Building 16 | CIP/SIP (EQUIPMENT REQUIREMENT – 200L) | PW | 2026-02-04 | 2026-02-07 | 0 | 0 | 0 | NA | 100 | PASSED | FALSE | WT-26-0016 | complete | pending
2026-02-03 | OCL22 | SV126.03 | PQ3-Week1 | TRUE | 16-2-010 | Building 16 | WATER SYSTEM (WFI) | PW | 2026-02-04 | 2026-02-07 | 0 | 0 | 0 | NA | 100 | PASSED | FALSE | WT-26-0016 | complete | pending
2026-02-03 | GOCL08 | SV127.01 | PQ3-Week1 | TRUE | WATER SYSTEM (B16) | Building 16 | Return loop (B16) | PW | 2026-02-04 | 2026-02-07 | 0 | 0 | 0 | NA | 100 | PASSED | FALSE | WT-26-0016 | complete | pending
2026-02-03 | GOCL03 | V50-11C (16) | PQ3-Week1 | TRUE | WATER SYSTEM (B16) | Building 16 | After RO (Before EDI) (B16) | RO water | 2026-02-04 | 2026-02-07 | 0 | 0 | 0 | NA | 500 | PASSED | FALSE | WT-26-0016 | complete | pending
2026-02-03 | GOCL04 | V50-39 (16) | PQ3-Week1 | TRUE | WATER SYSTEM (B16) | Building 16 | After EDI (B16) | PW | 2026-02-04 | 2026-02-07 | 0 | 0 | 0 | NA | 100 | PASSED | FALSE | WT-26-0016 | complete | pending
2026-02-03 | GOCL02 | V50-61 (16) | PQ3-Week1 | TRUE | WATER SYSTEM (B16) | Building 16 | After Cartridge filter 5 µm (B16) | PRW | 2026-02-04 | 2026-02-07 | 0 | 0 | 0 | NA | 500 | PASSED | FALSE | WT-26-0016 | complete | pending
2026-02-03 | GOCL01 | VB-05 (16) | PQ3-Week1 | TRUE | WATER SYSTEM (B16) | Building 16 | After Chlorine circulation tank (B16) | PRW | 2026-02-04 | 2026-02-07 | 0 | 0 | 0 | NA | 500 | PASSED | FALSE | WT-26-0016 | complete | pending
2026-02-03 | OLD29 | DV136.05 | PQ3-Week1 | TRUE | 12-3-037 | Building 12 | GLASSWARE WASHING 1 | PW | 2026-02-04 | 2026-02-07 | 0 | 0 | 0 | NA | 100 | PASSED | FALSE | WT-26-0017 | complete | pending
2026-02-03 | OLD30 | DV136.06 | PQ3-Week1 | TRUE | 12-3-037 | Building 12 | GLASSWARE WASHING 1 | PW | 2026-02-04 | 2026-02-07 | 0 | 0 | 0 | NA | 100 | PASSED | FALSE | WT-26-0017 | complete | pending
2026-02-03 | OLD26 | DV136.10 | PQ3-Week1 | TRUE | 12-3-056 | Building 12 | MEDIA PREPARATION | PW | 2026-02-04 | 2026-02-07 | 0 | 0 | 0 | NA | 100 | PASSED | FALSE | WT-26-0017 | complete | pending
2026-02-03 | OLD24 | DV136.11 | PQ3-Week1 | TRUE | 12-3-059 | Building 12 | AUTOCLAVE | PW | 2026-02-04 | 2026-02-07 | 0 | 0 | 0 | NA | 100 | PASSED | FALSE | WT-26-0017 | complete | pending
2026-02-03 | OLD25 | DV136.12 | PQ3-Week1 | TRUE | 12-3-056 | Building 12 | MEDIA PREPARATION | PW | 2026-02-04 | 2026-02-07 | 0 | 0 | 0 | NA | 100 | PASSED | FALSE | WT-26-0017 | complete | pending
2026-02-03 | OLD22 | DV136.13 | PQ3-Week1 | TRUE | 12-3-057 | Building 12 | STERILIZATION | PW | 2026-02-04 | 2026-02-07 | 0 | 0 | 0 | NA | 100 | PASSED | FALSE | WT-26-0017 | complete | pending
2026-02-03 | OLD27 | DV136.14 | PQ3-Week1 | TRUE | 12-3-074 | Building 12 | DECONTAMINATION | PW | 2026-02-04 | 2026-02-07 | 0 | 0 | 0 | NA | 100 | PASSED | FALSE | WT-26-0017 | complete | pending
2026-02-03 | OLD21 | DV136.15 | PQ3-Week1 | TRUE | 12-3-078 | Building 12 | GLASSWARE WASHING 2 | PW | 2026-02-04 | 2026-02-07 | 0 | 0 | 0 | NA | 100 | PASSED | FALSE | WT-26-0017 | complete | pending
2026-02-03 | OLD28 | DV136.18 | PQ3-Week1 | TRUE | 12-3-037 | Building 12 | GLASSWARE WASHING 1 | PW | 2026-02-04 | 2026-02-07 | 0 | 0 | 0 | NA | 100 | PASSED | FALSE | WT-26-0017 | complete | pending
2026-02-03 | OLD23 | SV136.18 | PQ3-Week1 | TRUE | 12-3-059 | Building 12 | AUTOCLAVE | PW | 2026-02-04 | 2026-02-07 | 0 | 0 | 0 | NA | 100 | PASSED | FALSE | WT-26-0017 | complete | pending
2026-02-03 | GOLD07 | SV137.01 | PQ3-Week1 | TRUE | WATER SYSTEM (B12) | Building 12 | Return loop (B12) | PW | 2026-02-04 | 2026-02-07 | 0 | 0 | 0 | NA | 100 | PASSED | FALSE | WT-26-0017 | complete | pending
2026-02-03 | GOLD03 | V50-11C (12) | PQ3-Week1 | TRUE | WATER SYSTEM (B12) | Building 12 | After RO (Before EDI) (B12) | RO water | 2026-02-04 | 2026-02-07 | 0 | 0 | 0 | NA | 500 | PASSED | FALSE | WT-26-0017 | complete | pending
2026-02-03 | GOLD04 | V50-39 (12) | PQ3-Week1 | TRUE | WATER SYSTEM (B12) | Building 12 | After EDI (B12) | PW | 2026-02-04 | 2026-02-07 | 0 | 0 | 0 | NA | 100 | PASSED | FALSE | WT-26-0017 | complete | pending
2026-02-03 | GOLD02 | V50-61 (12) | PQ3-Week1 | TRUE | WATER SYSTEM (B12) | Building 12 | After Cartridge filter 5 µm (B12) | PRW | 2026-02-04 | 2026-02-07 | 15 | 21 | 18 | NA | 500 | PASSED | FALSE | WT-26-0017 | complete | pending
2026-02-06 | BU19-14 | SV-14 | PQ3-Week1 | TRUE | PROCESS WATER (B19) | Building 19 | AFTER RO SYSTEM NO.12 SV14 | PRW | 2026-02-07 | 2026-02-10 | 0 | 0 | 0 | NA | 500 | PASSED | FALSE | WT-26-0018 | complete | pending
2026-02-06 | OSD12 | DV116.12 | PQ3-Week1 | TRUE | 10-3-078 | Building 10 | WASHING | PW | 2026-02-07 | 2026-02-10 | 0 | 0 | 0 | NA | 100 | PASSED | FALSE | WT-26-0019 | complete | pending
2026-02-06 | OSD11 | DV116.13 | PQ3-Week1 | TRUE | 10-3-078 | Building 10 | WASHING | PW | 2026-02-07 | 2026-02-10 | 0 | 0 | 0 | NA | 100 | PASSED | FALSE | WT-26-0019 | complete | pending
2026-02-06 | OSD09 | DV116.14 | PQ3-Week1 | TRUE | 10-3-086 | Building 10 | TOOL WASHING | PW | 2026-02-07 | 2026-02-10 | 0 | 0 | 0 | NA | 100 | PASSED | FALSE | WT-26-0019 | complete | pending
2026-02-06 | OSD28 | DV116.15 | PQ3-Week1 | TRUE | 10-3-104 | Building 10 | BINDER PREPARATION | PW | 2026-02-07 | 2026-02-10 | 0 | 0 | 0 | NA | 100 | PASSED | FALSE | WT-26-0019 | complete | pending
2026-02-06 | OSD07 | DV116.16 | PQ3-Week1 | TRUE | 10-3-107 | Building 10 | WET GRANULATION-2 | PW | 2026-02-07 | 2026-02-10 | 0 | 0 | 0 | NA | 100 | PASSED | FALSE | WT-26-0019 | complete | pending
2026-02-06 | OSD27 | DV116.17 | PQ3-Week1 | TRUE | 10-3-117 | Building 10 | IPQC-2 | PW | 2026-02-07 | 2026-02-10 | 0 | 0 | 0 | NA | 100 | PASSED | FALSE | WT-26-0019 | complete | pending
2026-02-06 | OSD06 | DV116.18 | PQ3-Week1 | TRUE | 10-3-111 | Building 10 | WET GRANULATION-5 | PW | 2026-02-07 | 2026-02-10 | 0 | 0 | 0 | NA | 100 | PASSED | FALSE | WT-26-0019 | complete | pending
2026-02-06 | OSD10 | SV116.09 | PQ3-Week1 | TRUE | 10-3-078 | Building 10 | WASHING | PW | 2026-02-07 | 2026-02-10 | 0 | 0 | 0 | NA | 100 | PASSED | FALSE | WT-26-0019 | complete | pending
2026-02-06 | OSD08 | SV116.11 | PQ3-Week1 | TRUE | 10-3-107 | Building 10 | WET GRANULATION-2 | PW | 2026-02-07 | 2026-02-10 | 0 | 0 | 0 | NA | 100 | PASSED | FALSE | WT-26-0019 | complete | pending
2026-02-06 | GOSD08 | SV117.01 | PQ3-Week1 | TRUE | WATER SYSTEM (B10) | Building 10 | Return loop (B10) | PW | 2026-02-07 | 2026-02-10 | 0 | 0 | 0 | NA | 100 | PASSED | FALSE | WT-26-0019 | complete | pending
2026-02-06 | GOSD04 | V50-11C(10) | PQ3-Week1 | TRUE | WATER SYSTEM (B10) | Building 10 | After RO (Before EDI) (B10) | RO water | 2026-02-07 | 2026-02-10 | 0 | 0 | 0 | NA | 500 | PASSED | FALSE | WT-26-0019 | complete | pending
2026-02-06 | GOSD05 | V50-39(10) | PQ3-Week1 | TRUE | WATER SYSTEM (B10) | Building 10 | After EDI (B10) | PW | 2026-02-07 | 2026-02-10 | 0 | 0 | 0 | NA | 100 | PASSED | FALSE | WT-26-0019 | complete | pending
2026-02-06 | GOSD03 | V50-61(10) | PQ3-Week1 | TRUE | WATER SYSTEM (B10) | Building 10 | After Cartridge filter 5 µm (B10) | PRW | 2026-02-07 | 2026-02-10 | 25 | 12 | 19 | NA | 500 | PASSED | FALSE | WT-26-0019 | complete | pending
2026-02-06 | GOSD01 | VB-05(10) | PQ3-Week1 | TRUE | WATER SYSTEM (B10) | Building 10 | After Chlorine circulation tank (B10) | PRW | 2026-02-07 | 2026-02-10 | 0 | 0 | 0 | NA | 500 | PASSED | FALSE | WT-26-0019 | complete | pending
2026-02-12 | OLD15 | DV136.02 | PQ3-Week2 | TRUE | 12-2-028 | Building 12 | ALCOHOL STORAGE | PW | 2026-02-13 | 2026-02-16 | 0 | 0 | 0 | NA | 100 | PASSED | FALSE | WT-26-0020 | complete | pending
2026-02-12 | OLD31 | DV136.07 | PQ3-Week2 | TRUE | 12-3-039 | Building 12 | INSTRUMENT 7 | PW | 2026-02-13 | 2026-02-16 | 0 | 0 | 0 | NA | 100 | PASSED | FALSE | WT-26-0020 | complete | pending
2026-02-12 | GOLD05 | SV133.01 | PQ3-Week2 | TRUE | WATER SYSTEM (B12) | Building 12 | After Storage tank (B12) | PW | 2026-02-13 | 2026-02-16 | 0 | 0 | 0 | NA | 100 | PASSED | FALSE | WT-26-0020 | complete | pending
2026-02-12 | GOLD06 | SV135.02 | PQ3-Week2 | TRUE | WATER SYSTEM (B12) | Building 12 | After UV (B12) | PW | 2026-02-13 | 2026-02-16 | 0 | 0 | 0 | NA | 100 | PASSED | FALSE | WT-26-0020 | complete | pending
2026-02-12 | OLD12 | SV136.03 | PQ3-Week2 | TRUE | 12-2-032 | Building 12 | CAMPHORATED OPIUM TINCTURE | PW | 2026-02-13 | 2026-02-16 | 0 | 0 | 0 | NA | 100 | PASSED | FALSE | WT-26-0020 | complete | pending
2026-02-12 | OLD14 | SV136.04 | PQ3-Week2 | TRUE | 12-2-030 | Building 12 | OPIUM TINCTURE | PW | 2026-02-13 | 2026-02-16 | 0 | 0 | 0 | NA | 100 | PASSED | FALSE | WT-26-0020 | complete | pending
2026-02-12 | OLD13 | SV136.05 | PQ3-Week2 | TRUE | 12-2-032 | Building 12 | CAMPHORATED OPIUM TINCTURE | PW | 2026-02-13 | 2026-02-16 | 1 | 0 | 1 | NA | 100 | PASSED | FALSE | WT-26-0020 | complete | pending
2026-02-12 | OLD05 | SV136.06 | PQ3-Week2 | TRUE | 12-2-034 | Building 12 | SYRUP PREPARATION | PW | 2026-02-13 | 2026-02-16 | 0 | 0 | 0 | NA | 100 | PASSED | FALSE | WT-26-0020 | complete | pending
2026-02-12 | OLD04 | SV136.07 | PQ3-Week2 | TRUE | 12-2-034 | Building 12 | SYRUP PREPARATION | PW | 2026-02-13 | 2026-02-16 | 0 | 0 | 0 | NA | 100 | PASSED | FALSE | WT-26-0020 | complete | pending
2026-02-12 | OLD03 | SV136.12 | PQ3-Week2 | TRUE | 12-2-036 | Building 12 | CIP 1 | PW | 2026-02-13 | 2026-02-16 | 0 | 0 | 0 | NA | 100 | PASSED | FALSE | WT-26-0020 | complete | pending
2026-02-12 | GOLD07 | SV137.01 | PQ3-Week2 | TRUE | WATER SYSTEM (B12) | Building 12 | Return loop (B12) | PW | 2026-02-13 | 2026-02-16 | 0 | 0 | 0 | NA | 100 | PASSED | FALSE | WT-26-0020 | complete | pending
2026-02-12 | OCL21 | DV126.05 | PQ3-Week2 | TRUE | 16-3-054 | Building 16 | WASHING | PW | 2026-02-13 | 2026-02-16 | 0 | 0 | 0 | NA | 100 | PASSED | FALSE | WT-26-0021 | complete | pending
2026-02-12 | OCL14 | DV126.11 | PQ3-Week2 | TRUE | 16-3-073 | Building 16 | MFG 4 (5000L) | PW | 2026-02-13 | 2026-02-16 | 0 | 0 | 0 | NA | 100 | PASSED | FALSE | WT-26-0021 | complete | pending
2026-02-12 | GOCL05 | SV123.01 | PQ3-Week2 | TRUE | WATER SYSTEM (B16) | Building 16 | After Storage tank (B16) | PW | 2026-02-13 | 2026-02-16 | 0 | 0 | 0 | NA | 100 | PASSED | FALSE | WT-26-0021 | complete | pending
2026-02-12 | GOCL07 | SV125.02 | PQ3-Week2 | TRUE | WATER SYSTEM (B16) | Building 16 | After UV (B16) | PW | 2026-02-13 | 2026-02-16 | 10 | 33 | 22 | NA | 100 | PASSED | FALSE | WT-26-0021 | complete | pending
2026-02-12 | OCL23 | SV126.04 | PQ3-Week2 | TRUE | 16-2-010 | Building 16 | WATER SYSTEM (PSG) | PW | 2026-02-13 | 2026-02-16 | 0 | 0 | 0 | NA | 100 | PASSED | FALSE | WT-26-0021 | complete | pending
2026-02-12 | OCL15 | SV126.14 | PQ3-Week2 | TRUE | 16-3-073 | Building 16 | MFG 4 (400L) | PW | 2026-02-13 | 2026-02-16 | 0 | 0 | 0 | NA | 100 | PASSED | FALSE | WT-26-0021 | complete | pending
2026-02-12 | OCL17 | SV126.15 | PQ3-Week2 | TRUE | 16-3-075 | Building 16 | MFG 5 PROCESS (2000L) | PW | 2026-02-13 | 2026-02-16 | 25 | 16 | 21 | NA | 100 | PASSED | FALSE | WT-26-0021 | complete | pending
2026-02-12 | OCL13 | SV126.19 | PQ3-Week2 | TRUE | 16-3-087 | Building 16 | CIP 2 (EQUIPMENT REQUIREMENT) | PW | 2026-02-13 | 2026-02-16 | 0 | 0 | 0 | NA | 100 | PASSED | FALSE | WT-26-0021 | complete | pending
2026-02-12 | GOCL08 | SV127.01 | PQ3-Week2 | TRUE | WATER SYSTEM (B16) | Building 16 | Return loop (B16) | PW | 2026-02-13 | 2026-02-16 | 0 | 0 | 0 | NA | 100 | PASSED | FALSE | WT-26-0021 | complete | pending
2026-02-13 | OSD36 | DV116.03 | PQ3-Week2 | TRUE | 10-2-034 | Building 10 | SAMPLE PREPARATION | PW | 2026-02-14 | 2026-02-17 | 0 | 0 | 0 | NA | 100 | PASSED | FALSE | WT-26-0022 | complete | pending
2026-02-13 | OSD40 | DV116.04 | PQ3-Week2 | TRUE | 10-2-037 | Building 10 | SKID FOR BIN WASHING-1 | PW | 2026-02-14 | 2026-02-17 | 0 | 0 | 0 | NA | 100 | PASSED | FALSE | WT-26-0022 | complete | pending
2026-02-13 | OSD39 | DV116.05 | PQ3-Week2 | TRUE | 10-2-032 | Building 10 | GLASS-WARE WASHING | PW | 2026-02-14 | 2026-02-17 | 0 | 0 | 0 | NA | 100 | PASSED | FALSE | WT-26-0022 | complete | pending
2026-02-13 | OSD37 | DV116.06 | PQ3-Week2 | TRUE | 10-2-034 | Building 10 | SAMPLE PREPARATION | PW | 2026-02-14 | 2026-02-17 | 0 | 0 | 0 | NA | 100 | PASSED | FALSE | WT-26-0022 | complete | pending
2026-02-13 | OSD38 | DV116.07 | PQ3-Week2 | TRUE | 10-2-032 | Building 10 | GLASS-WARE WASHING | PW | 2026-02-14 | 2026-02-17 | 0 | 0 | 0 | NA | 100 | PASSED | FALSE | WT-26-0022 | complete | pending
2026-02-13 | OSD25 | DV116.08 | PQ3-Week2 | TRUE | 10-3-059 | Building 10 | COATING SOLUTION PREP.-1 | PW | 2026-02-14 | 2026-02-17 | 0 | 0 | 0 | NA | 100 | PASSED | FALSE | WT-26-0022 | complete | pending
2026-02-13 | OSD24 | DV116.09 | PQ3-Week2 | TRUE | 10-3-060 | Building 10 | COATING SOLUTION PREP.-2 | PW | 2026-02-14 | 2026-02-17 | 0 | 0 | 0 | NA | 100 | PASSED | FALSE | WT-26-0022 | complete | pending
2026-02-13 | OSD31 | DV116.10 | PQ3-Week2 | TRUE | 10-3-065 | Building 10 | COATING SOLUTION PREP.-3 | PW | 2026-02-14 | 2026-02-17 | 0 | 0 | 0 | NA | 100 | PASSED | FALSE | WT-26-0022 | complete | pending
2026-02-13 | OSD30 | DV116.11 | PQ3-Week2 | TRUE | 10-3-066 | Building 10 | COATING SOLUTION PREP.-4 | PW | 2026-02-14 | 2026-02-17 | 0 | 0 | 0 | NA | 100 | PASSED | FALSE | WT-26-0022 | complete | pending
2026-02-13 | GOSD06 | SV113.01 | PQ3-Week2 | TRUE | WATER SYSTEM (B10) | Building 10 | After Storage tank (B10) | PW | 2026-02-14 | 2026-02-17 | 0 | 0 | 0 | NA | 100 | PASSED | FALSE | WT-26-0022 | complete | pending
2026-02-13 | GOSD07 | SV115.02 | PQ3-Week2 | TRUE | WATER SYSTEM (B10) | Building 10 | After UV (B10) | PW | 2026-02-14 | 2026-02-17 | 0 | 0 | 0 | NA | 100 | PASSED | FALSE | WT-26-0022 | complete | pending
2026-02-13 | OSD26 | SV116.03 | PQ3-Week2 | TRUE | 10-3-058 | Building 10 | COATING ROOM-1 | PW | 2026-02-14 | 2026-02-17 | 0 | 0 | 0 | NA | 100 | PASSED | FALSE | WT-26-0022 | complete | pending
2026-02-13 | OSD23 | SV116.04 | PQ3-Week2 | TRUE | 10-3-061 | Building 10 | COATING ROOM-2 | PW | 2026-02-14 | 2026-02-17 | 0 | 0 | 0 | NA | 100 | PASSED | FALSE | WT-26-0022 | complete | pending
2026-02-13 | OSD22 | SV116.05 | PQ3-Week2 | TRUE | 10-3-062 | Building 10 | COATING ROOM-3 | PW | 2026-02-14 | 2026-02-17 | 0 | 0 | 0 | NA | 100 | PASSED | FALSE | WT-26-0022 | complete | pending
2026-02-13 | OSD33 | SV116.06 | PQ3-Week2 | TRUE | 10-3-063 | Building 10 | COATING ROOM-4 | PW | 2026-02-14 | 2026-02-17 | 0 | 0 | 0 | NA | 100 | PASSED | FALSE | WT-26-0022 | complete | pending
2026-02-13 | OSD32 | SV116.07 | PQ3-Week2 | TRUE | 10-3-064 | Building 10 | COATING ROOM-5 | PW | 2026-02-14 | 2026-02-17 | 0 | 0 | 0 | NA | 100 | PASSED | FALSE | WT-26-0022 | complete | pending
2026-02-13 | OSD29 | SV116.08 | PQ3-Week2 | TRUE | 10-3-067 | Building 10 | COATING ROOM-6 | PW | 2026-02-14 | 2026-02-17 | 0 | 0 | 0 | NA | 100 | PASSED | FALSE | WT-26-0022 | complete | pending
2026-02-13 | GOSD08 | SV117.01 | PQ3-Week2 | TRUE | WATER SYSTEM (B10) | Building 10 | Return loop (B10) | PW | 2026-02-14 | 2026-02-17 | 0 | 0 | 0 | NA | 100 | PASSED | FALSE | WT-26-0022 | complete | pending
2026-02-17 | OCL24 | DV126.04 | PQ3-Week3 | TRUE | 16-2-010 | Building 16 | WATER SYSTEM (PW) | PW | 2026-02-18 | 2026-02-21 | 0 | 0 | 0 |  | 100 | PASSED | FALSE | WT-26-0023 | complete | pending
2026-02-17 | OCL08 | DV126.09 | PQ3-Week3 | TRUE | 16-3-090 | Building 16 | CIP 1 (ZINK WASHING) | PW | 2026-02-18 | 2026-02-21 | 0 | 0 | 0 |  | 100 | PASSED | FALSE | WT-26-0023 | complete | pending
2026-02-17 | OCL20 | SV126.05 | PQ3-Week3 | TRUE | 16-3-049 | Building 16 | LINEN WASHING | PW | 2026-02-18 | 2026-02-21 | 0 | 0 | 0 |  | 100 | PASSED | FALSE | WT-26-0023 | complete | pending
2026-02-17 | OCL06 | SV126.06 | PQ3-Week3 | TRUE | 16-3-067 | Building 16 | MFG 1 | PW | 2026-02-18 | 2026-02-21 | 0 | 0 | 0 |  | 100 | PASSED | FALSE | WT-26-0023 | complete | pending
2026-02-17 | OCL16 | SV126.18 | PQ3-Week3 | TRUE | 16-3-085 | Building 16 | CIP 3 (EQUIPMENT REQUIREMENT) | PW | 2026-02-18 | 2026-02-21 | 0 | 0 | 0 |  | 100 | PASSED | FALSE | WT-26-0023 | complete | pending
2026-02-17 | OCL07 | SV126.21 | PQ3-Week3 | TRUE | 16-3-090 | Building 16 | CIP 1 (EQUIPMENT REQUIREMENT) | PW | 2026-02-18 | 2026-02-21 | 0 | 0 | 0 |  | 100 | PASSED | FALSE | WT-26-0023 | complete | pending
2026-02-17 | GOCL08 | SV127.01 | PQ3-Week3 | TRUE | WATER SYSTEM (B16) | Building 16 | Return loop (B16) | PW | 2026-02-18 | 2026-02-21 | 0 | 0 | 0 |  | 100 | PASSED | FALSE | WT-26-0023 | complete | pending
2026-02-17 | GOCL03 | V50-11C (16) | PQ3-Week3 | TRUE | WATER SYSTEM (B16) | Building 16 | After RO (Before EDI) (B16) | RO water | 2026-02-18 | 2026-02-21 | 0 | 0 | 0 |  | 500 | PASSED | FALSE | WT-26-0023 | complete | pending
2026-02-17 | GOCL04 | V50-39 (16) | PQ3-Week3 | TRUE | WATER SYSTEM (B16) | Building 16 | After EDI (B16) | PW | 2026-02-18 | 2026-02-21 | 0 | 0 | 0 |  | 100 | PASSED | FALSE | WT-26-0023 | complete | pending
2026-02-17 | GOCL02 | V50-61 (16) | PQ3-Week3 | TRUE | WATER SYSTEM (B16) | Building 16 | After Cartridge filter 5 µm (B16) | PRW | 2026-02-18 | 2026-02-21 | 0 | 0 | 0 |  | 500 | PASSED | FALSE | WT-26-0023 | complete | pending
2026-02-17 | GOCL01 | VB-05 (16) | PQ3-Week3 | TRUE | WATER SYSTEM (B16) | Building 16 | After Chlorine circulation tank (B16) | PRW | 2026-02-18 | 2026-02-21 | 1 | 1 | 1 |  | 500 | PASSED | FALSE | WT-26-0023 | complete | pending
2026-02-17 | OLD19 | DV136.01 | PQ3-Week3 | TRUE | 12-1-035 | Building 12 | SUGAR TRANSFERRING | PW | 2026-02-18 | 2026-02-21 | 0 | 0 | 0 |  | 100 | PASSED | FALSE | WT-26-0024 | complete | pending
2026-02-17 | OLD17 | DV136.03 | PQ3-Week3 | TRUE | 12-2-053 | Building 12 | IPQC | PW | 2026-02-18 | 2026-02-21 | 0 | 0 | 0 |  | 100 | PASSED | FALSE | WT-26-0024 | complete | pending
2026-02-17 | OLD34 | DV136.04 | PQ3-Week3 | TRUE | 12-2-077 | Building 12 | WATER SYSTEM ROOM | PW | 2026-02-18 | 2026-02-21 | 0 | 0 | 0 |  | 100 | PASSED | FALSE | WT-26-0024 | complete | pending
2026-02-17 | OLD20 | DV136.16 | PQ3-Week3 | TRUE | 12-1-064 | Building 12 | WASHING | PW | 2026-02-18 | 2026-02-21 | 0 | 0 | 0 |  | 100 | PASSED | FALSE | WT-26-0024 | complete | pending
2026-02-17 | OLD01 | DV136.17 | PQ3-Week3 | TRUE | 12-2-065 | Building 12 | WASHING | PW | 2026-02-18 | 2026-02-21 | 0 | 0 | 0 |  | 100 | PASSED | FALSE | WT-26-0024 | complete | pending
2026-02-17 | OLD10 | SV136.15 | PQ3-Week3 | TRUE | 12-2-055 | Building 12 | CIP 3 | PW | 2026-02-18 | 2026-02-21 | 0 | 0 | 0 |  | 100 | PASSED | FALSE | WT-26-0024 | complete | pending
2026-02-17 | OLD02 | SV136.16 | PQ3-Week3 | TRUE | 12-2-057 | Building 12 | CIP 2 | PW | 2026-02-18 | 2026-02-21 | 0 | 0 | 0 |  | 100 | PASSED | FALSE | WT-26-0024 | complete | pending
2026-02-17 | GOLD07 | SV137.01 | PQ3-Week3 | TRUE | WATER SYSTEM (B12) | Building 12 | Return loop (B12) | PW | 2026-02-18 | 2026-02-21 | 0 | 0 | 0 |  | 100 | PASSED | FALSE | WT-26-0024 | complete | pending
2026-02-17 | GOLD03 | V50-11C (12) | PQ3-Week3 | TRUE | WATER SYSTEM (B12) | Building 12 | After RO (Before EDI) (B12) | RO water | 2026-02-18 | 2026-02-21 | 0 | 0 | 0 |  | 500 | PASSED | FALSE | WT-26-0024 | complete | pending
2026-02-17 | GOLD04 | V50-39 (12) | PQ3-Week3 | TRUE | WATER SYSTEM (B12) | Building 12 | After EDI (B12) | PW | 2026-02-18 | 2026-02-21 | 0 | 0 | 0 |  | 100 | PASSED | FALSE | WT-26-0024 | complete | pending
2026-02-17 | GOLD02 | V50-61 (12) | PQ3-Week3 | TRUE | WATER SYSTEM (B12) | Building 12 | After Cartridge filter 5 µm (B12) | PRW | 2026-02-18 | 2026-02-21 | 0 | 0 | 0 |  | 500 | PASSED | FALSE | WT-26-0024 | complete | pending
2026-02-20 | BU19-14 | SV-14 | PQ3-Week3 | TRUE | PROCESS WATER (B19) | Building 19 | AFTER RO SYSTEM NO.12 SV14 | PRW | 2026-02-21 | 2026-02-24 | 0 | 0 | 0 |  | 500 | PASSED | FALSE | WT-26-0025 | complete | pending
2026-02-20 | OSD42 | DV116.01 | PQ3-Week3 | TRUE | 10-1-057 | Building 10 | WASHING-P | PW | 2026-02-21 | 2026-02-24 | 0 | 0 | 0 |  | 100 | PASSED | FALSE | WT-26-0026 | complete | pending
2026-02-20 | OSD41 | DV116.02 | PQ3-Week3 | TRUE | 10-1-115 | Building 10 | WASHING | PW | 2026-02-21 | 2026-02-24 | 0 | 0 | 0 |  | 100 | PASSED | FALSE | WT-26-0026 | complete | pending
2026-02-20 | OSD20 | DV116.19 | PQ3-Week3 | TRUE | 10-3-143 | Building 10 | COATING SOLUTION PREP.-P | PW | 2026-02-21 | 2026-02-24 | 0 | 0 | 0 |  | 100 | PASSED | FALSE | WT-26-0026 | complete | pending
2026-02-20 | OSD19 | DV116.20 | PQ3-Week3 | TRUE | 10-3-149 | Building 10 | IPQC-1-P | PW | 2026-02-21 | 2026-02-24 | 0 | 0 | 0 |  | 100 | PASSED | FALSE | WT-26-0026 | complete | pending
2026-02-20 | OSD16 | DV116.21 | PQ3-Week3 | TRUE | 10-3-152 | Building 10 | WASHING-P | PW | 2026-02-21 | 2026-02-24 | 0 | 0 | 0 |  | 100 | PASSED | FALSE | WT-26-0026 | complete | pending
2026-02-20 | OSD17 | DV116.22 | PQ3-Week3 | TRUE | 10-3-152 | Building 10 | WASHING-P | PW | 2026-02-21 | 2026-02-24 | 0 | 0 | 0 |  | 100 | PASSED | FALSE | WT-26-0026 | complete | pending
2026-02-20 | OSD15 | DV116.23 | PQ3-Week3 | TRUE | 10-3-159 | Building 10 | BINDER PREPARATION-P | PW | 2026-02-21 | 2026-02-24 | 0 | 0 | 0 |  | 100 | PASSED | FALSE | WT-26-0026 | complete | pending
2026-02-20 | OSD14 | DV116.24 | PQ3-Week3 | TRUE | 10-3-163 | Building 10 | WET GRANULATION 1-P | PW | 2026-02-21 | 2026-02-24 | 0 | 0 | 0 |  | 100 | PASSED | FALSE | WT-26-0026 | complete | pending
2026-02-20 | OSD13 | DV116.25 | PQ3-Week3 | TRUE | 10-3-171 | Building 10 | TOOL WASHING-P | PW | 2026-02-21 | 2026-02-24 | 0 | 0 | 0 |  | 100 | PASSED | FALSE | WT-26-0026 | complete | pending
2026-02-20 | OSD21 | SV116.12 | PQ3-Week3 | TRUE | 10-3-144 | Building 10 | COATING-P | PW | 2026-02-21 | 2026-02-24 | 0 | 0 | 0 |  | 100 | PASSED | FALSE | WT-26-0026 | complete | pending
2026-02-20 | OSD18 | SV116.13 | PQ3-Week3 | TRUE | 10-3-152 | Building 10 | WASHING-P | PW | 2026-02-21 | 2026-02-24 | 0 | 0 | 0 |  | 100 | PASSED | FALSE | WT-26-0026 | complete | pending
2026-02-20 | GOSD08 | SV117.01 | PQ3-Week3 | TRUE | WATER SYSTEM (B10) | Building 10 | Return loop (B10) | PW | 2026-02-21 | 2026-02-24 | 0 | 0 | 0 |  | 100 | PASSED | FALSE | WT-26-0026 | complete | pending
2026-02-20 | GOSD04 | V50-11C(10) | PQ3-Week3 | TRUE | WATER SYSTEM (B10) | Building 10 | After RO (Before EDI) (B10) | RO water | 2026-02-21 | 2026-02-24 | 0 | 0 | 0 |  | 500 | PASSED | FALSE | WT-26-0026 | complete | pending
2026-02-20 | GOSD02 | V50-60(10) | PQ3-Week3 | TRUE | WATER SYSTEM (B10) | Building 10 | Before Cartridge filter 5 µm (B10) | PRW | 2026-02-21 | 2026-02-24 | 0 | 0 | 0 |  | 500 | PASSED | FALSE | WT-26-0026 | complete | pending
2026-02-20 | GOSD03 | V50-61(10) | PQ3-Week3 | TRUE | WATER SYSTEM (B10) | Building 10 | After Cartridge filter 5 µm (B10) | PRW | 2026-02-21 | 2026-02-24 | 0 | 0 | 0 |  | 500 | PASSED | FALSE | WT-26-0026 | complete | pending
2026-02-20 | GOSD01 | VB-05(10) | PQ3-Week3 | TRUE | WATER SYSTEM (B10) | Building 10 | After Chlorine circulation tank (B10) | PRW | 2026-02-21 | 2026-02-24 | 0 | 0 | 0 |  | 500 | PASSED | FALSE | WT-26-0026 | complete | pending
2026-02-27 | OSD43 | DV116.26 | PQ3-Week4 | TRUE | 10-4-015 | Building 10 | WATER SYSTEM ROOM | PW | 2026-02-28 | 2026-03-03 | 0 | 0 | 0 |  | 100 | PASSED | FALSE | WT-26-0027 | complete | pending
2026-02-27 | GOSD06 | SV113.01 | PQ3-Week4 | TRUE | WATER SYSTEM (B10) | Building 10 | After Storage tank (B10) | PW | 2026-02-28 | 2026-03-03 | 0 | 0 | 0 |  | 100 | PASSED | FALSE | WT-26-0027 | complete | pending
2026-02-27 | GOSD07 | SV115.02 | PQ3-Week4 | TRUE | WATER SYSTEM (B10) | Building 10 | After UV (B10) | PW | 2026-02-28 | 2026-03-03 | 0 | 0 | 0 |  | 100 | PASSED | FALSE | WT-26-0027 | complete | pending
2026-02-27 | OSD35 | SV116.01 | PQ3-Week4 | TRUE | 10-2-021 | Building 10 | INSTRUMENT-1 | PW | 2026-02-28 | 2026-03-03 | 0 | 0 | 0 |  | 100 | PASSED | FALSE | WT-26-0027 | complete | pending
2026-02-27 | OSD34 | SV116.02 | PQ3-Week4 | TRUE | 10-2-037 | Building 10 | SKID FOR BIN WASHING-2 | PW | 2026-02-28 | 2026-03-03 | 0 | 0 | 0 |  | 100 | PASSED | FALSE | WT-26-0027 | complete | pending
2026-02-27 | OSD01 | SV116.15 | PQ3-Week4 | TRUE | 10-4-012 | Building 10 | CIP SKID-1 FOR BIN WASHING-1 | PW | 2026-02-28 | 2026-03-03 | 0 | 0 | 0 |  | 100 | PASSED | FALSE | WT-26-0027 | complete | pending
2026-02-27 | OSD02 | SV116.16 | PQ3-Week4 | TRUE | 10-4-012 | Building 10 | WIP SKID-3 FOR GRANULATION POTENT | PW | 2026-02-28 | 2026-03-03 | 0 | 0 | 0 |  | 100 | PASSED | FALSE | WT-26-0027 | complete | pending
2026-02-27 | OSD03 | SV116.17 | PQ3-Week4 | TRUE | 10-4-012 | Building 10 | CIP SKID-2 FOR BIN WASHING-1 | PW | 2026-02-28 | 2026-03-03 | 0 | 0 | 0 |  | 100 | PASSED | FALSE | WT-26-0027 | complete | pending
2026-02-27 | OSD04 | SV116.18 | PQ3-Week4 | TRUE | 10-4-012 | Building 10 | WIP SKID-1 FOR GRANULATION NON POTENT | PW | 2026-02-28 | 2026-03-03 | 0 | 0 | 0 |  | 100 | PASSED | FALSE | WT-26-0027 | complete | pending
2026-02-27 | OSD05 | SV116.19 | PQ3-Week4 | TRUE | 10-4-012 | Building 10 | WIP SKID-2 FOR GRANULATION NON POTENT | PW | 2026-02-28 | 2026-03-03 | 0 | 0 | 0 |  | 100 | PASSED | FALSE | WT-26-0027 | complete | pending
2026-02-27 | GOSD08 | SV117.01 | PQ3-Week4 | TRUE | WATER SYSTEM (B10) | Building 10 | Return loop (B10) | PW | 2026-02-28 | 2026-03-03 | 0 | 0 | 0 |  | 100 | PASSED | FALSE | WT-26-0027 | complete | pending
2026-02-25 | OLD32 | DV136.08 | PQ3-Week4 | TRUE | 12-3-042 | Building 12 | SAMPLE PREPARATION | PW | 2026-02-26 | 2026-03-02 | 0 | 0 | 0 |  | 100 | PASSED | FALSE | WT-26-0028 | complete | pending
2026-02-25 | OLD33 | DV136.09 | PQ3-Week4 | TRUE | 12-3-042 | Building 12 | SAMPLE PREPARATION | PW | 2026-02-26 | 2026-03-02 | 0 | 13 | 7 |  | 100 | PASSED | FALSE | WT-26-0028 | complete | pending
2026-02-25 | GOLD05 | SV133.01 | PQ3-Week4 | TRUE | WATER SYSTEM (B12) | Building 12 | After Storage tank (B12) | PW | 2026-02-26 | 2026-03-02 | 0 | 0 | 0 |  | 100 | PASSED | FALSE | WT-26-0028 | complete | pending
2026-02-25 | GOLD06 | SV135.02 | PQ3-Week4 | TRUE | WATER SYSTEM (B12) | Building 12 | After UV (B12) | PW | 2026-02-26 | 2026-03-02 | 0 | 0 | 0 |  | 100 | PASSED | FALSE | WT-26-0028 | complete | pending
2026-02-25 | OLD18 | SV136.02 | PQ3-Week4 | TRUE | 12-2-024 | Building 12 | LIQUORICE EXTRACT | PW | 2026-02-26 | 2026-03-02 | 0 | 0 | 0 |  | 100 | PASSED | FALSE | WT-26-0028 | complete | pending
2026-02-25 | OLD11 | SV136.08 | PQ3-Week4 | TRUE | 12-2-043 | Building 12 | MFG 3 | PW | 2026-02-26 | 2026-03-02 | 0 | 0 | 0 |  | 100 | PASSED | FALSE | WT-26-0028 | complete | pending
2026-02-25 | OLD06 | SV136.09 | PQ3-Week4 | TRUE | 12-2-039 | Building 12 | MFG 1 | PW | 2026-02-26 | 2026-03-02 | 0 | 0 | 0 |  | 100 | PASSED | TRUE | WT-26-0028 | complete | pending
2026-02-25 | OLD07 | SV136.10 | PQ3-Week4 | TRUE | 12-2-041 | Building 12 | MFG 2 | PW | 2026-02-26 | 2026-03-02 | 0 | 0 | 0 |  | 100 | PASSED | FALSE | WT-26-0028 | complete | pending
2026-02-25 | OLD08 | SV136.11 | PQ3-Week4 | TRUE | 12-2-043 | Building 12 | MFG 3 | PW | 2026-02-26 | 2026-03-02 | 0 | 0 | 0 |  | 100 | PASSED | FALSE | WT-26-0028 | complete | pending
2026-02-25 | OLD09 | SV136.13 | PQ3-Week4 | TRUE | 12-2-043 | Building 12 | MFG 3 | PW | 2026-02-26 | 2026-03-02 | 0 | 0 | 0 |  | 100 | PASSED | FALSE | WT-26-0028 | complete | pending
2026-02-25 | OLD16 | SV136.14 | PQ3-Week4 | TRUE | 12-2-045 | Building 12 | MFG 4 | PW | 2026-02-26 | 2026-03-02 | 0 | 0 | 0 |  | 100 | PASSED | FALSE | WT-26-0028 | complete | pending
2026-02-25 | GOLD07 | SV137.01 | PQ3-Week4 | TRUE | WATER SYSTEM (B12) | Building 12 | Return loop (B12) | PW | 2026-02-26 | 2026-03-02 | 0 | 0 | 0 |  | 100 | PASSED | FALSE | WT-26-0028 | complete | pending
2026-02-25 | OCL10 | DV126.06 | PQ3-Week4 | TRUE | 16-3-069 | Building 16 | MFG 2 | PW | 2026-02-26 | 2026-03-02 | 0 | 0 | 0 |  | 100 | PASSED | FALSE | WT-26-0029 | complete | pending
2026-02-25 | OCL19 | DV126.07 | PQ3-Week4 | TRUE | 16-3-077 | Building 16 | MFG 6 | PW | 2026-02-26 | 2026-03-02 | 0 | 0 | 0 |  | 100 | PASSED | FALSE | WT-26-0029 | complete | pending
2026-02-25 | OCL18 | DV126.08 | PQ3-Week4 | TRUE | 16-3-077 | Building 16 | MFG 6 | PW | 2026-02-26 | 2026-03-02 | 0 | 0 | 0 |  | 100 | PASSED | FALSE | WT-26-0029 | complete | pending
2026-02-25 | OCL09 | DV126.10 | PQ3-Week4 | TRUE | 16-3-069 | Building 16 | MFG 2 | PW | 2026-02-26 | 2026-03-02 | 0 | 0 | 0 |  | 100 | PASSED | FALSE | WT-26-0029 | complete | pending
2026-02-25 | GOCL05 | SV123.01 | PQ3-Week4 | TRUE | WATER SYSTEM (B16) | Building 16 | After Storage tank (B16) | PW | 2026-02-26 | 2026-03-02 | 0 | 0 | 0 |  | 100 | PASSED | FALSE | WT-26-0029 | complete | pending
2026-02-25 | GOCL07 | SV125.02 | PQ3-Week4 | TRUE | WATER SYSTEM (B16) | Building 16 | After UV (B16) | PW | 2026-02-26 | 2026-03-02 | 0 | 0 | 0 |  | 100 | PASSED | FALSE | WT-26-0029 | complete | pending
2026-02-25 | OCL12 | SV126.09 | PQ3-Week4 | TRUE | 16-3-071 | Building 16 | MFG 3 (5000L) | PW | 2026-02-26 | 2026-03-02 | 0 | 0 | 0 |  | 100 | PASSED | FALSE | WT-26-0029 | complete | pending
2026-02-25 | OCL11 | SV126.10 | PQ3-Week4 | TRUE | 16-3-071 | Building 16 | MFG 3 (1200L) | PW | 2026-02-26 | 2026-03-02 | 97 | 96 | 97 |  | 100 | PASSED | FALSE | WT-26-0029 | complete | pending
2026-02-25 | GOCL08 | SV127.01 | PQ3-Week4 | TRUE | WATER SYSTEM (B16) | Building 16 | Return loop (B16) | PW | 2026-02-26 | 2026-03-02 | 0 | 0 | 0 |  | 100 | PASSED | FALSE | WT-26-0029 | complete | pending
2026-03-05 | OCL02 | DV126.01 | PQ3-Week1 | TRUE | 16-1-082 | Building 16 | WASHING | PW | 2026-03-06 | 2026-03-10 | 0 | 0 | 0 |  | 100 | PASSED | FALSE | WT-26-0030 | complete | pending
2026-03-05 | OCL01 | DV126.02 | PQ3-Week1 | TRUE | 16-1-082 | Building 16 | WASHING | PW | 2026-03-06 | 2026-03-10 | 0 | 0 | 0 |  | 100 | PASSED | FALSE | WT-26-0030 | complete | pending
2026-03-05 | OCL04 | DV126.03 | PQ3-Week1 | TRUE | 16-1-098 | Building 16 | CIP/SIP (SINK WASHING) | PW | 2026-03-06 | 2026-03-10 | 0 | 0 | 0 |  | 100 | PASSED | FALSE | WT-26-0030 | complete | pending
2026-03-05 | GOCL08 | SV127.01 | PQ3-Week1 | TRUE | WATER SYSTEM (B16) | Building 16 | Return loop (B16) | PW | 2026-03-06 | 2026-03-10 | 0 | 0 | 0 |  | 100 | PASSED | FALSE | WT-26-0030 | complete | pending
2026-03-05 | OCL05 | SV126.01 | PQ3-Week1 | TRUE | 16-1-092 | Building 16 | LINEN WASHING | PW | 2026-03-06 | 2026-03-10 | 0 | 0 | 0 |  | 100 | PASSED | FALSE | WT-26-0030 | complete | pending
2026-03-05 | OCL03 | SV126.02 | PQ3-Week1 | TRUE | 16-1-098 | Building 16 | CIP/SIP (EQUIPMENT REQUIREMENT – 200L) | PW | 2026-03-06 | 2026-03-10 | 0 | 0 | 0 |  | 100 | PASSED | FALSE | WT-26-0030 | complete | pending
2026-03-05 | OCL22 | SV126.03 | PQ3-Week1 | TRUE | 16-2-010 | Building 16 | WATER SYSTEM (WFI) | PW | 2026-03-06 | 2026-03-10 | 0 | 0 | 0 |  | 100 | PASSED | FALSE | WT-26-0030 | complete | pending
2026-03-05 | GOCL03 | V50-11C (16) | PQ3-Week1 | TRUE | WATER SYSTEM (B16) | Building 16 | After RO (Before EDI) (B16) | RO water | 2026-03-06 | 2026-03-10 | 88 | 74 | 81 |  | 500 | PASSED | FALSE | WT-26-0030 | complete | pending
2026-03-05 | GOCL04 | V50-39 (16) | PQ3-Week1 | TRUE | WATER SYSTEM (B16) | Building 16 | After EDI (B16) | PW | 2026-03-06 | 2026-03-10 | 0 | 0 | 0 |  | 100 | PASSED | FALSE | WT-26-0030 | complete | pending
2026-03-05 | GOCL02 | V50-61 (16) | PQ3-Week1 | TRUE | WATER SYSTEM (B16) | Building 16 | After Cartridge filter 5 µm (B16) | PRW | 2026-03-06 | 2026-03-10 | 0 | 0 | 0 |  | 500 | PASSED | FALSE | WT-26-0030 | complete | pending
2026-03-05 | GOCL01 | VB-05 (16) | PQ3-Week1 | TRUE | WATER SYSTEM (B16) | Building 16 | After Chlorine circulation tank (B16) | PRW | 2026-03-06 | 2026-03-10 | 0 | 0 | 0 |  | 500 | PASSED | FALSE | WT-26-0030 | complete | pending
2026-03-05 | OLD29 | DV136.05 | PQ3-Week1 | TRUE | 12-3-037 | Building 12 | GLASSWARE WASHING 1 | PW | 2026-03-06 | 2026-03-10 | 0 | 0 | 0 |  | 100 | PASSED | FALSE | WT-26-0031 | complete | pending
2026-03-05 | OLD30 | DV136.06 | PQ3-Week1 | TRUE | 12-3-037 | Building 12 | GLASSWARE WASHING 1 | PW | 2026-03-06 | 2026-03-10 | 0 | 0 | 0 |  | 100 | PASSED | FALSE | WT-26-0031 | complete | pending
2026-03-05 | OLD26 | DV136.10 | PQ3-Week1 | TRUE | 12-3-056 | Building 12 | MEDIA PREPARATION | PW | 2026-03-06 | 2026-03-10 | 0 | 0 | 0 |  | 100 | PASSED | FALSE | WT-26-0031 | complete | pending
2026-03-05 | OLD24 | DV136.11 | PQ3-Week1 | TRUE | 12-3-059 | Building 12 | AUTOCLAVE | PW | 2026-03-06 | 2026-03-10 | 0 | 0 | 0 |  | 100 | PASSED | FALSE | WT-26-0031 | complete | pending
2026-03-05 | OLD25 | DV136.12 | PQ3-Week1 | TRUE | 12-3-056 | Building 12 | MEDIA PREPARATION | PW | 2026-03-06 | 2026-03-10 | 0 | 0 | 0 |  | 100 | PASSED | FALSE | WT-26-0031 | complete | pending
2026-03-05 | OLD22 | DV136.13 | PQ3-Week1 | TRUE | 12-3-057 | Building 12 | STERILIZATION | PW | 2026-03-06 | 2026-03-10 | 0 | 0 | 0 |  | 100 | PASSED | FALSE | WT-26-0031 | complete | pending
2026-03-05 | OLD27 | DV136.14 | PQ3-Week1 | TRUE | 12-3-074 | Building 12 | DECONTAMINATION | PW | 2026-03-06 | 2026-03-10 | 0 | 0 | 0 |  | 100 | PASSED | FALSE | WT-26-0031 | complete | pending
2026-03-05 | OLD21 | DV136.15 | PQ3-Week1 | TRUE | 12-3-078 | Building 12 | GLASSWARE WASHING 2 | PW | 2026-03-06 | 2026-03-10 | 0 | 0 | 0 |  | 100 | PASSED | FALSE | WT-26-0031 | complete | pending
2026-03-05 | OLD28 | DV136.18 | PQ3-Week1 | TRUE | 12-3-037 | Building 12 | GLASSWARE WASHING 1 | PW | 2026-03-06 | 2026-03-10 | 0 | 0 | 0 |  | 100 | PASSED | FALSE | WT-26-0031 | complete | pending
2026-03-05 | OLD23 | SV136.18 | PQ3-Week1 | TRUE | 12-3-059 | Building 12 | AUTOCLAVE | PW | 2026-03-06 | 2026-03-10 | 0 | 0 | 0 |  | 100 | PASSED | FALSE | WT-26-0031 | complete | pending
2026-03-05 | GOLD07 | SV137.01 | PQ3-Week1 | TRUE | WATER SYSTEM (B12) | Building 12 | Return loop (B12) | PW | 2026-03-06 | 2026-03-10 | 0 | 0 | 0 |  | 100 | PASSED | FALSE | WT-26-0031 | complete | pending
2026-03-05 | GOLD03 | V50-11C (12) | PQ3-Week1 | TRUE | WATER SYSTEM (B12) | Building 12 | After RO (Before EDI) (B12) | RO water | 2026-03-06 | 2026-03-10 | 0 | 0 | 0 |  | 500 | PASSED | FALSE | WT-26-0031 | complete | pending
2026-03-05 | GOLD04 | V50-39 (12) | PQ3-Week1 | TRUE | WATER SYSTEM (B12) | Building 12 | After EDI (B12) | PW | 2026-03-06 | 2026-03-10 | 0 | 0 | 0 |  | 100 | PASSED | FALSE | WT-26-0031 | complete | pending
2026-03-05 | GOLD02 | V50-61 (12) | PQ3-Week1 | TRUE | WATER SYSTEM (B12) | Building 12 | After Cartridge filter 5 µm (B12) | PRW | 2026-03-06 | 2026-03-10 | 54 | 32 | 43 |  | 500 | PASSED | FALSE | WT-26-0031 | complete | pending
2026-03-05 | GOLD01 | VB-05 (12) | PQ3-Week1 | TRUE | WATER SYSTEM (B12) | Building 12 | After Chlorine circulation tank | PRW | 2026-03-06 | 2026-03-10 |  |  | #DIV/0! | ไม่มีตรวจ (Already checked log book) | 500 | NA | FALSE | WT-26-0031 | complete | pending
2026-03-06 | BU19-14 | SV-14 | PQ3-Week1 | TRUE | PROCESS WATER (B19) | Building 19 | AFTER RO SYSTEM NO.12 SV14 | PRW | 2026-03-07 | 2026-03-10 | 0 | 0 | 0 |  | 500 | PASSED | FALSE | WT-26-0032 | complete | pending
2026-03-06 | OSD12 | DV116.12 | PQ3-Week1 | TRUE | 10-3-078 | Building 10 | WASHING | PW | 2026-03-07 | 2026-03-10 | 0 | 0 | 0 |  | 100 | PASSED | FALSE | WT-26-0033 | complete | pending
2026-03-06 | OSD11 | DV116.13 | PQ3-Week1 | TRUE | 10-3-078 | Building 10 | WASHING | PW | 2026-03-07 | 2026-03-10 | 0 | 0 | 0 |  | 100 | PASSED | FALSE | WT-26-0033 | complete | pending
2026-03-06 | OSD09 | DV116.14 | PQ3-Week1 | TRUE | 10-3-086 | Building 10 | TOOL WASHING | PW | 2026-03-07 | 2026-03-10 | 0 | 0 | 0 |  | 100 | PASSED | FALSE | WT-26-0033 | complete | pending
2026-03-06 | OSD28 | DV116.15 | PQ3-Week1 | TRUE | 10-3-104 | Building 10 | BINDER PREPARATION | PW | 2026-03-07 | 2026-03-10 | 11 | 13 | 12 |  | 100 | PASSED | FALSE | WT-26-0033 | complete | pending
2026-03-06 | OSD07 | DV116.16 | PQ3-Week1 | TRUE | 10-3-107 | Building 10 | WET GRANULATION-2 | PW | 2026-03-07 | 2026-03-10 | 0 | 0 | 0 |  | 100 | PASSED | FALSE | WT-26-0033 | complete | pending
2026-03-06 | OSD27 | DV116.17 | PQ3-Week1 | TRUE | 10-3-117 | Building 10 | IPQC-2 | PW | 2026-03-07 | 2026-03-10 | 0 | 0 | 0 |  | 100 | PASSED | FALSE | WT-26-0033 | complete | pending
2026-03-06 | OSD06 | DV116.18 | PQ3-Week1 | TRUE | 10-3-111 | Building 10 | WET GRANULATION-5 | PW | 2026-03-07 | 2026-03-10 | 0 | 0 | 0 |  | 100 | PASSED | FALSE | WT-26-0033 | complete | pending
2026-03-06 | OSD10 | SV116.09 | PQ3-Week1 | TRUE | 10-3-078 | Building 10 | WASHING | PW | 2026-03-07 | 2026-03-10 | 0 | 0 | 0 |  | 100 | PASSED | FALSE | WT-26-0033 | complete | pending
2026-03-06 | OSD08 | SV116.11 | PQ3-Week1 | TRUE | 10-3-107 | Building 10 | WET GRANULATION-2 | PW | 2026-03-07 | 2026-03-10 | 0 | 0 | 0 |  | 100 | PASSED | FALSE | WT-26-0033 | complete | pending
2026-03-06 | GOSD08 | SV117.01 | PQ3-Week1 | TRUE | WATER SYSTEM (B10) | Building 10 | Return loop (B10) | PW | 2026-03-07 | 2026-03-10 | 0 | 0 | 0 |  | 100 | PASSED | FALSE | WT-26-0033 | complete | pending
2026-03-06 | GOSD04 | V50-11C(10) | PQ3-Week1 | TRUE | WATER SYSTEM (B10) | Building 10 | After RO (Before EDI) (B10) | RO water | 2026-03-07 | 2026-03-10 | 0 | 0 | 0 |  | 500 | PASSED | FALSE | WT-26-0033 | complete | pending
2026-03-06 | GOSD05 | V50-39(10) | PQ3-Week1 | TRUE | WATER SYSTEM (B10) | Building 10 | After EDI (B10) | PW | 2026-03-07 | 2026-03-10 | 0 | 0 | 0 |  | 100 | PASSED | FALSE | WT-26-0033 | complete | pending
2026-03-06 | GOSD03 | V50-61(10) | PQ3-Week1 | TRUE | WATER SYSTEM (B10) | Building 10 | After Cartridge filter 5 µm (B10) | PRW | 2026-03-07 | 2026-03-10 | 20 | 29 | 25 |  | 500 | PASSED | FALSE | WT-26-0033 | complete | pending
2026-03-06 | GOSD01 | VB-05(10) | PQ3-Week1 | TRUE | WATER SYSTEM (B10) | Building 10 | After Chlorine circulation tank (B10) | PRW | 2026-03-07 | 2026-03-10 | 1 | 4 | 3 |  | 500 | PASSED | FALSE | WT-26-0033 | complete | pending
2026-01-16 | BU11 | #N/A | PQ3-Week2 | TRUE | #N/A | #N/A | #N/A | #N/A | 2026-01-17 | 2026-01-20 | 0 | 0 | 0 | NA | #N/A | NA | FALSE | WT-26-0073 | complete | synced
2026-02-13 | B11 | #N/A | PQ3-Week2 | TRUE | #N/A | #N/A | #N/A | #N/A | 2026-02-14 | 2026-02-17 | 0 | 0 | 0 | NA | #N/A | NA | FALSE | WT-26-0074 | complete | synced
2026-03-09 | OCL02 | DV126.01 | Speacial | TRUE | 16-1-082 | Building 16 | WASHING | PW | 2026-03-10 | 2026-03-13 | 0 | 0 | 0 | shutdown 36 hr. | 100 | PASSED | FALSE | WT-26-0075 | complete | synced
2026-03-09 | OCL01 | DV126.02 | Speacial | TRUE | 16-1-082 | Building 16 | WASHING | PW | 2026-03-10 | 2026-03-13 | 0 | 0 | 0 | shutdown 36 hr. | 100 | PASSED | FALSE | WT-26-0075 | complete | synced
2026-03-09 | OCL04 | DV126.03 | Speacial | TRUE | 16-1-098 | Building 16 | CIP/SIP (SINK WASHING) | PW | 2026-03-10 | 2026-03-13 | 0 | 0 | 0 | shutdown 36 hr. | 100 | PASSED | FALSE | WT-26-0075 | complete | synced
2026-03-09 | OCL24 | DV126.04 | Speacial | TRUE | 16-2-010 | Building 16 | WATER SYSTEM (PW) | PW | 2026-03-10 | 2026-03-13 | 0 | 0 | 0 | shutdown 36 hr. | 100 | PASSED | FALSE | WT-26-0075 | complete | synced
2026-03-09 | OCL21 | DV126.05 | Speacial | TRUE | 16-3-054 | Building 16 | WASHING | PW | 2026-03-10 | 2026-03-13 | 21 | 16 | 19 | shutdown 36 hr. | 100 | PASSED | FALSE | WT-26-0075 | complete | synced
2026-03-09 | OCL10 | DV126.06 | Speacial | TRUE | 16-3-069 | Building 16 | MFG 2 | PW | 2026-03-10 | 2026-03-13 | 0 | 0 | 0 | shutdown 36 hr. | 100 | PASSED | FALSE | WT-26-0075 | complete | synced
2026-03-09 | OCL19 | DV126.07 | Speacial | TRUE | 16-3-077 | Building 16 | MFG 6 | PW | 2026-03-10 | 2026-03-13 | 0 | 0 | 0 | shutdown 36 hr. | 100 | PASSED | FALSE | WT-26-0075 | complete | synced
2026-03-09 | OCL18 | DV126.08 | Speacial | TRUE | 16-3-077 | Building 16 | MFG 6 | PW | 2026-03-10 | 2026-03-13 | 0 | 0 | 0 | shutdown 36 hr. | 100 | PASSED | FALSE | WT-26-0075 | complete | synced
2026-03-09 | OCL08 | DV126.09 | Speacial | TRUE | 16-3-090 | Building 16 | CIP 1 (ZINK WASHING) | PW | 2026-03-10 | 2026-03-13 | 0 | 0 | 0 | shutdown 36 hr. | 100 | PASSED | FALSE | WT-26-0075 | complete | synced
2026-03-09 | OCL09 | DV126.10 | Speacial | TRUE | 16-3-069 | Building 16 | MFG 2 | PW | 2026-03-10 | 2026-03-13 | 0 | 0 | 0 | shutdown 36 hr. | 100 | PASSED | FALSE | WT-26-0075 | complete | synced
2026-03-09 | OCL14 | DV126.11 | Speacial | TRUE | 16-3-073 | Building 16 | MFG 4 (5000L) | PW | 2026-03-10 | 2026-03-13 | 0 | 0 | 0 | shutdown 36 hr. | 100 | PASSED | FALSE | WT-26-0075 | complete | synced
2026-03-09 | GOCL05 | SV123.01 | Speacial | TRUE | WATER SYSTEM (B16) | Building 16 | After Storage tank (B16) | PW | 2026-03-10 | 2026-03-13 | 0 | 0 | 0 | shutdown 36 hr. (เช้า) | 100 | PASSED | FALSE | WT-26-0075 | complete | synced
2026-03-09 | GOCL05 | SV123.01 | Speacial | TRUE | WATER SYSTEM (B16) | Building 16 | After Storage tank (B16) | PW | 2026-03-10 | 2026-03-13 | 0 | 0 | 0 | shutdown 36 hr. | 100 | PASSED | FALSE | WT-26-0075 | complete | synced
2026-03-09 | OCL05 | SV126.01 | Speacial | TRUE | 16-1-092 | Building 16 | LINEN WASHING | PW | 2026-03-10 | 2026-03-13 | 0 | 0 | 0 | shutdown 36 hr. | 100 | PASSED | FALSE | WT-26-0075 | complete | synced
2026-03-09 | OCL03 | SV126.02 | Speacial | TRUE | 16-1-098 | Building 16 | CIP/SIP (EQUIPMENT REQUIREMENT – 200L) | PW | 2026-03-10 | 2026-03-13 | 0 | 0 | 0 | shutdown 36 hr. | 100 | PASSED | FALSE | WT-26-0075 | complete | synced
2026-03-09 | OCL22 | SV126.03 | Speacial | TRUE | 16-2-010 | Building 16 | WATER SYSTEM (WFI) | PW | 2026-03-10 | 2026-03-13 | 0 | 0 | 0 | shutdown 36 hr. | 100 | PASSED | FALSE | WT-26-0075 | complete | synced
2026-03-09 | OCL23 | SV126.04 | Speacial | TRUE | 16-2-010 | Building 16 | WATER SYSTEM (PSG) | PW | 2026-03-10 | 2026-03-13 | 0 | 0 | 0 | shutdown 36 hr. | 100 | PASSED | FALSE | WT-26-0075 | complete | synced
2026-03-09 | OCL20 | SV126.05 | Speacial | TRUE | 16-3-049 | Building 16 | LINEN WASHING | PW | 2026-03-10 | 2026-03-13 | 0 | 0 | 0 | shutdown 36 hr. | 100 | PASSED | FALSE | WT-26-0075 | complete | synced
2026-03-09 | OCL06 | SV126.06 | Speacial | TRUE | 16-3-067 | Building 16 | MFG 1 | PW | 2026-03-10 | 2026-03-13 | 0 | 0 | 0 | shutdown 36 hr. | 100 | PASSED | FALSE | WT-26-0075 | complete | synced
2026-03-09 | OCL12 | SV126.09 | Speacial | TRUE | 16-3-071 | Building 16 | MFG 3 (5000L) | PW | 2026-03-10 | 2026-03-13 | 0 | 0 | 0 | shutdown 36 hr. | 100 | PASSED | FALSE | WT-26-0075 | complete | synced
2026-03-09 | OCL11 | SV126.10 | Speacial | TRUE | 16-3-071 | Building 16 | MFG 3 (1200L) | PW | 2026-03-10 | 2026-03-13 | 0 | 0 | 0 | shutdown 36 hr. | 100 | PASSED | FALSE | WT-26-0075 | complete | synced
2026-03-09 | OCL17 | SV126.15 | Speacial | TRUE | 16-3-075 | Building 16 | MFG 5 PROCESS (2000L) | PW | 2026-03-10 | 2026-03-13 | 0 | 0 | 0 | shutdown 36 hr. | 100 | PASSED | FALSE | WT-26-0075 | complete | synced
2026-03-09 | OCL16 | SV126.18 | Speacial | TRUE | 16-3-085 | Building 16 | CIP 3 (EQUIPMENT REQUIREMENT) | PW | 2026-03-10 | 2026-03-13 | 0 | 0 | 0 | shutdown 36 hr. | 100 | PASSED | FALSE | WT-26-0075 | complete | synced
2026-03-09 | OCL13 | SV126.19 | Speacial | TRUE | 16-3-087 | Building 16 | CIP 2 (EQUIPMENT REQUIREMENT) | PW | 2026-03-10 | 2026-03-13 | 0 | 0 | 0 | shutdown 36 hr. | 100 | PASSED | FALSE | WT-26-0075 | complete | synced
2026-03-09 | OCL07 | SV126.21 | Speacial | TRUE | 16-3-090 | Building 16 | CIP 1 (EQUIPMENT REQUIREMENT) | PW | 2026-03-10 | 2026-03-13 | 0 | 0 | 0 | shutdown 36 hr. | 100 | PASSED | FALSE | WT-26-0075 | complete | synced
2026-03-09 | GOCL08 | SV127.01 | Speacial | TRUE | WATER SYSTEM (B16) | Building 16 | Return loop (B16) | PW | 2026-03-10 | 2026-03-13 | 0 | 0 | 0 | shutdown 36 hr. (เช้า) | 100 | PASSED | FALSE | WT-26-0075 | complete | synced
2026-03-09 | GOCL08 | SV127.01 | Speacial | TRUE | WATER SYSTEM (B16) | Building 16 | Return loop (B16) | PW | 2026-03-10 | 2026-03-13 | 0 | 0 | 0 | shutdown 36 hr. | 100 | PASSED | FALSE | WT-26-0075 | complete | synced
2026-03-09 | GOCL04 | V50-39 (16) | Speacial | TRUE | WATER SYSTEM (B16) | Building 16 | After EDI (B16) | PW | 2026-03-10 | 2026-03-13 | 0 | 0 | 0 | shutdown 36 hr. | 100 | PASSED | FALSE | WT-26-0075 | complete | synced
2026-03-11 | GOLD05 | SV133.01 | PQ3-Week2 | TRUE | WATER SYSTEM (B12) | Building 12 | After Storage tank (B12) | PW | 2026-03-12 | 2026-03-15 | 0 | 0 | 0 |  | 100 | PASSED | FALSE | WT-26-0034 | complete | pending
2026-03-11 | GOLD06 | SV135.02 | PQ3-Week2 | TRUE | WATER SYSTEM (B12) | Building 12 | After UV (B12) | PW | 2026-03-12 | 2026-03-15 | 0 | 0 | 0 |  | 100 | PASSED | FALSE | WT-26-0034 | complete | pending
2026-03-11 | GOLD07 | SV137.01 | PQ3-Week2 | TRUE | WATER SYSTEM (B12) | Building 12 | Return loop (B12) | PW | 2026-03-12 | 2026-03-15 | 0 | 0 | 0 |  | 100 | PASSED | FALSE | WT-26-0034 | complete | pending
2026-03-11 | OLD03 | SV136.12 | PQ3-Week2 | TRUE | 12-2-036 | Building 12 | CIP 1 | PW | 2026-03-12 | 2026-03-15 | 0 | 0 | 0 |  | 100 | PASSED | FALSE | WT-26-0034 | complete | pending
2026-03-11 | OLD04 | SV136.07 | PQ3-Week2 | TRUE | 12-2-034 | Building 12 | SYRUP PREPARATION | PW | 2026-03-12 | 2026-03-15 | 0 | 0 | 0 |  | 100 | PASSED | FALSE | WT-26-0034 | complete | pending
2026-03-11 | OLD05 | SV136.06 | PQ3-Week2 | TRUE | 12-2-034 | Building 12 | SYRUP PREPARATION | PW | 2026-03-12 | 2026-03-15 | 0 | 0 | 0 |  | 100 | PASSED | FALSE | WT-26-0034 | complete | pending
2026-03-11 | OLD12 | SV136.03 | PQ3-Week2 | TRUE | 12-2-032 | Building 12 | CAMPHORATED OPIUM TINCTURE | PW | 2026-03-12 | 2026-03-15 | 0 | 0 | 0 |  | 100 | PASSED | FALSE | WT-26-0034 | complete | pending
2026-03-11 | OLD13 | SV136.05 | PQ3-Week2 | TRUE | 12-2-032 | Building 12 | CAMPHORATED OPIUM TINCTURE | PW | 2026-03-12 | 2026-03-15 | 0 | 0 | 0 |  | 100 | PASSED | FALSE | WT-26-0034 | complete | pending
2026-03-11 | OLD14 | SV136.04 | PQ3-Week2 | TRUE | 12-2-030 | Building 12 | OPIUM TINCTURE | PW | 2026-03-12 | 2026-03-15 | 0 | 0 | 0 |  | 100 | PASSED | FALSE | WT-26-0034 | complete | pending
2026-03-11 | OLD15 | DV136.02 | PQ3-Week2 | TRUE | 12-2-028 | Building 12 | ALCOHOL STORAGE | PW | 2026-03-12 | 2026-03-15 | 0 | 0 | 0 |  | 100 | PASSED | FALSE | WT-26-0034 | complete | pending
2026-03-11 | OLD31 | DV136.07 | PQ3-Week2 | TRUE | 12-3-039 | Building 12 | INSTRUMENT 7 | PW | 2026-03-12 | 2026-03-15 | 0 | 0 | 0 |  | 100 | PASSED | FALSE | WT-26-0034 | complete | pending
2026-03-13 | B11 | #N/A |  | TRUE | #N/A | #N/A | #N/A | #N/A | 2026-03-14 | 2026-03-17 | 0 | 0 | 0 |  | #N/A | NA | FALSE | WT-26-0042 | complete | pending
2026-03-13 | GOSD06 | SV113.01 | PQ3-Week2 | TRUE | WATER SYSTEM (B10) | Building 10 | After Storage tank (B10) | PW | 2026-03-14 | 2026-03-17 | 0 | 0 | 0 |  | 100 | PASSED | FALSE | WT-26-0042 | complete | pending
2026-03-13 | GOSD07 | SV115.02 | PQ3-Week2 | TRUE | WATER SYSTEM (B10) | Building 10 | After UV (B10) | PW | 2026-03-14 | 2026-03-17 | 0 | 0 | 0 |  | 100 | PASSED | FALSE | WT-26-0042 | complete | pending
2026-03-13 | GOSD08 | SV117.01 | PQ3-Week2 | TRUE | WATER SYSTEM (B10) | Building 10 | Return loop (B10) | PW | 2026-03-14 | 2026-03-17 | 0 | 0 | 0 |  | 100 | PASSED | FALSE | WT-26-0042 | complete | pending
2026-03-13 | OSD22 | SV116.05 | PQ3-Week2 | TRUE | 10-3-062 | Building 10 | COATING ROOM-3 | PW | 2026-03-14 | 2026-03-17 | 0 | 0 | 0 |  | 100 | PASSED | FALSE | WT-26-0042 | complete | pending
2026-03-13 | OSD23 | SV116.04 | PQ3-Week2 | TRUE | 10-3-061 | Building 10 | COATING ROOM-2 | PW | 2026-03-14 | 2026-03-17 | 0 | 0 | 0 |  | 100 | PASSED | FALSE | WT-26-0042 | complete | pending
2026-03-13 | OSD24 | DV116.09 | PQ3-Week2 | TRUE | 10-3-060 | Building 10 | COATING SOLUTION PREP.-2 | PW | 2026-03-14 | 2026-03-17 | 0 | 0 | 0 |  | 100 | PASSED | FALSE | WT-26-0042 | complete | pending
2026-03-13 | OSD25 | DV116.08 | PQ3-Week2 | TRUE | 10-3-059 | Building 10 | COATING SOLUTION PREP.-1 | PW | 2026-03-14 | 2026-03-17 | 0 | 0 | 0 |  | 100 | PASSED | FALSE | WT-26-0042 | complete | pending
2026-03-13 | OSD26 | SV116.03 | PQ3-Week2 | TRUE | 10-3-058 | Building 10 | COATING ROOM-1 | PW | 2026-03-14 | 2026-03-17 | 0 | 0 | 0 |  | 100 | PASSED | FALSE | WT-26-0042 | complete | pending
2026-03-13 | OSD29 | SV116.08 | PQ3-Week2 | TRUE | 10-3-067 | Building 10 | COATING ROOM-6 | PW | 2026-03-14 | 2026-03-17 | 0 | 0 | 0 |  | 100 | PASSED | FALSE | WT-26-0042 | complete | pending
2026-03-13 | OSD30 | DV116.11 | PQ3-Week2 | TRUE | 10-3-066 | Building 10 | COATING SOLUTION PREP.-4 | PW | 2026-03-14 | 2026-03-17 | 0 | 0 | 0 |  | 100 | PASSED | FALSE | WT-26-0042 | complete | pending
2026-03-13 | OSD31 | DV116.10 | PQ3-Week2 | TRUE | 10-3-065 | Building 10 | COATING SOLUTION PREP.-3 | PW | 2026-03-14 | 2026-03-17 | 0 | 0 | 0 |  | 100 | PASSED | FALSE | WT-26-0042 | complete | pending
2026-03-13 | OSD32 | SV116.07 | PQ3-Week2 | TRUE | 10-3-064 | Building 10 | COATING ROOM-5 | PW | 2026-03-14 | 2026-03-17 | 0 | 0 | 0 |  | 100 | PASSED | FALSE | WT-26-0042 | complete | pending
2026-03-13 | OSD33 | SV116.06 | PQ3-Week2 | TRUE | 10-3-063 | Building 10 | COATING ROOM-4 | PW | 2026-03-14 | 2026-03-17 | 0 | 0 | 0 |  | 100 | PASSED | FALSE | WT-26-0042 | complete | pending
2026-03-13 | OSD36 | DV116.03 | PQ3-Week2 | TRUE | 10-2-034 | Building 10 | SAMPLE PREPARATION | PW | 2026-03-14 | 2026-03-17 | 0 | 0 | 0 |  | 100 | PASSED | FALSE | WT-26-0042 | complete | pending
2026-03-13 | OSD37 | DV116.06 | PQ3-Week2 | TRUE | 10-2-034 | Building 10 | SAMPLE PREPARATION | PW | 2026-03-14 | 2026-03-17 | 0 | 0 | 0 |  | 100 | PASSED | FALSE | WT-26-0042 | complete | pending
2026-03-13 | OSD38 | DV116.07 | PQ3-Week2 | TRUE | 10-2-032 | Building 10 | GLASS-WARE WASHING | PW | 2026-03-14 | 2026-03-17 | 0 | 0 | 0 |  | 100 | PASSED | FALSE | WT-26-0042 | complete | pending
2026-03-13 | OSD39 | DV116.05 | PQ3-Week2 | TRUE | 10-2-032 | Building 10 | GLASS-WARE WASHING | PW | 2026-03-14 | 2026-03-17 | 0 | 0 | 0 |  | 100 | PASSED | FALSE | WT-26-0042 | complete | pending
2026-03-13 | OSD40 | DV116.04 | PQ3-Week2 | TRUE | 10-2-037 | Building 10 | SKID FOR BIN WASHING-1 | PW | 2026-03-14 | 2026-03-17 | 0 | 0 | 0 |  | 100 | PASSED | FALSE | WT-26-0042 | complete | pending
2026-03-17 | GOLD02 | V50-61 (12) | PQ3-Week3 | TRUE | WATER SYSTEM (B12) | Building 12 | After Cartridge filter 5 µm (B12) | PRW | 2026-03-18 | 2026-03-21 | 71 | 130 | 101 |  | 500 | PASSED | FALSE | WT-26-0035 | complete | pending
2026-03-17 | GOLD03 | V50-11C (12) | PQ3-Week3 | TRUE | WATER SYSTEM (B12) | Building 12 | After RO (Before EDI) (B12) | RO water | 2026-03-18 | 2026-03-21 | 0 | 0 | 0 |  | 500 | PASSED | FALSE | WT-26-0035 | complete | pending
2026-03-17 | GOLD04 | V50-39 (12) | PQ3-Week3 | TRUE | WATER SYSTEM (B12) | Building 12 | After EDI (B12) | PW | 2026-03-18 | 2026-03-21 | 0 | 0 | 0 |  | 100 | PASSED | FALSE | WT-26-0035 | complete | pending
2026-03-17 | GOLD07 | SV137.01 | PQ3-Week3 | TRUE | WATER SYSTEM (B12) | Building 12 | Return loop (B12) | PW | 2026-03-18 | 2026-03-21 | 0 | 0 | 0 |  | 100 | PASSED | FALSE | WT-26-0035 | complete | pending
2026-03-17 | OLD01 | DV136.17 | PQ3-Week3 | TRUE | 12-2-065 | Building 12 | WASHING | PW | 2026-03-18 | 2026-03-21 | 0 | 0 | 0 |  | 100 | PASSED | FALSE | WT-26-0035 | complete | pending
2026-03-17 | OLD02 | SV136.16 | PQ3-Week3 | TRUE | 12-2-057 | Building 12 | CIP 2 | PW | 2026-03-18 | 2026-03-21 | 0 | 0 | 0 |  | 100 | PASSED | FALSE | WT-26-0035 | complete | pending
2026-03-17 | OLD10 | SV136.15 | PQ3-Week3 | TRUE | 12-2-055 | Building 12 | CIP 3 | PW | 2026-03-18 | 2026-03-21 | 0 | 0 | 0 |  | 100 | PASSED | FALSE | WT-26-0035 | complete | pending
2026-03-17 | OLD17 | DV136.03 | PQ3-Week3 | TRUE | 12-2-053 | Building 12 | IPQC | PW | 2026-03-18 | 2026-03-21 | 0 | 0 | 0 |  | 100 | PASSED | FALSE | WT-26-0035 | complete | pending
2026-03-17 | OLD19 | DV136.01 | PQ3-Week3 | TRUE | 12-1-035 | Building 12 | SUGAR TRANSFERRING | PW | 2026-03-18 | 2026-03-21 | 0 | 0 | 0 |  | 100 | PASSED | FALSE | WT-26-0035 | complete | pending
2026-03-17 | OLD20 | DV136.16 | PQ3-Week3 | TRUE | 12-1-064 | Building 12 | WASHING | PW | 2026-03-18 | 2026-03-21 | 0 | 0 | 0 |  | 100 | PASSED | FALSE | WT-26-0035 | complete | pending
2026-03-17 | OLD34 | DV136.04 | PQ3-Week3 | TRUE | 12-2-077 | Building 12 | WATER SYSTEM ROOM | PW | 2026-03-18 | 2026-03-21 | 0 | 0 | 0 |  | 100 | PASSED | FALSE | WT-26-0035 | complete | pending
2026-03-17 | GOCL01 | VB-05 (16) | PQ3-Week3 | TRUE | WATER SYSTEM (B16) | Building 16 | After Chlorine circulation tank (B16) | PRW | 2026-03-18 | 2026-03-21 | 145 | 138 | 142 |  | 500 | PASSED | FALSE | WT-26-0036 | complete | pending
2026-03-17 | GOCL02 | V50-61 (16) | PQ3-Week3 | TRUE | WATER SYSTEM (B16) | Building 16 | After Cartridge filter 5 µm (B16) | PRW | 2026-03-18 | 2026-03-21 | 159 | 286 | 223 |  | 500 | PASSED | FALSE | WT-26-0036 | complete | pending
2026-03-17 | GOCL03 | V50-11C (16) | PQ3-Week3 | TRUE | WATER SYSTEM (B16) | Building 16 | After RO (Before EDI) (B16) | RO water | 2026-03-18 | 2026-03-21 | 0 | 0 | 0 |  | 500 | PASSED | FALSE | WT-26-0036 | complete | pending
2026-03-17 | GOCL04 | V50-39 (16) | PQ3-Week3 | TRUE | WATER SYSTEM (B16) | Building 16 | After EDI (B16) | PW | 2026-03-18 | 2026-03-21 | 0 | 0 | 0 |  | 100 | PASSED | FALSE | WT-26-0036 | complete | pending
2026-03-17 | GOCL08 | SV127.01 | PQ3-Week3 | TRUE | WATER SYSTEM (B16) | Building 16 | Return loop (B16) | PW | 2026-03-18 | 2026-03-21 | 0 | 0 | 0 |  | 100 | PASSED | FALSE | WT-26-0036 | complete | pending
2026-03-17 | OCL06 | SV126.06 | PQ3-Week3 | TRUE | 16-3-067 | Building 16 | MFG 1 | PW | 2026-03-18 | 2026-03-21 | 0 | 0 | 0 |  | 100 | PASSED | FALSE | WT-26-0036 | complete | pending
2026-03-17 | OCL07 | SV126.21 | PQ3-Week3 | TRUE | 16-3-090 | Building 16 | CIP 1 (EQUIPMENT REQUIREMENT) | PW | 2026-03-18 | 2026-03-21 | 0 | 0 | 0 |  | 100 | PASSED | FALSE | WT-26-0036 | complete | pending
2026-03-17 | OCL08 | DV126.09 | PQ3-Week3 | TRUE | 16-3-090 | Building 16 | CIP 1 (ZINK WASHING) | PW | 2026-03-18 | 2026-03-21 | 0 | 0 | 0 |  | 100 | PASSED | FALSE | WT-26-0036 | complete | pending
2026-03-17 | OCL16 | SV126.18 | PQ3-Week3 | TRUE | 16-3-085 | Building 16 | CIP 3 (EQUIPMENT REQUIREMENT) | PW | 2026-03-18 | 2026-03-21 | 0 | 0 | 0 |  | 100 | PASSED | FALSE | WT-26-0036 | complete | pending
2026-03-17 | OCL20 | SV126.05 | PQ3-Week3 | TRUE | 16-3-049 | Building 16 | LINEN WASHING | PW | 2026-03-18 | 2026-03-21 | 0 | 0 | 0 |  | 100 | PASSED | FALSE | WT-26-0036 | complete | pending
2026-03-17 | OCL24 | DV126.04 | PQ3-Week3 | TRUE | 16-2-010 | Building 16 | WATER SYSTEM (PW) | PW | 2026-03-18 | 2026-03-21 | 0 | 0 | 0 |  | 100 | PASSED | FALSE | WT-26-0036 | complete | pending
2026-03-20 | BU19-14 | SV-14 | PQ3-Week3 | TRUE | PROCESS WATER (B19) | Building 19 | AFTER RO SYSTEM NO.12 SV14 | PRW | 2026-03-21 | 2026-03-24 | 0 | 0 | 0 |  | 500 | PASSED | FALSE | WT-26-0037 | complete | pending
2026-03-20 | GOSD01 | VB-05(10) | PQ3-Week3 | TRUE | WATER SYSTEM (B10) | Building 10 | After Chlorine circulation tank (B10) | PRW | 2026-03-21 | 2026-03-24 | 32 | 56 | 44 |  | 500 | PASSED | FALSE | WT-26-0038 | complete | pending
2026-03-20 | GOSD03 | V50-61(10) | PQ3-Week3 | TRUE | WATER SYSTEM (B10) | Building 10 | After Cartridge filter 5 µm (B10) | PRW | 2026-03-21 | 2026-03-24 | 134 | 116 | 125 |  | 500 | PASSED | FALSE | WT-26-0038 | complete | pending
2026-03-20 | GOSD04 | V50-11C(10) | PQ3-Week3 | TRUE | WATER SYSTEM (B10) | Building 10 | After RO (Before EDI) (B10) | RO water | 2026-03-21 | 2026-03-24 | 0 | 0 | 0 |  | 500 | PASSED | FALSE | WT-26-0038 | complete | pending
2026-03-20 | GOSD05 | V50-39(10) | PQ3-Week3 | TRUE | WATER SYSTEM (B10) | Building 10 | After EDI (B10) | PW | 2026-03-21 | 2026-03-24 | 0 | 0 | 0 |  | 100 | PASSED | FALSE | WT-26-0038 | complete | pending
2026-03-20 | GOSD08 | SV117.01 | PQ3-Week3 | TRUE | WATER SYSTEM (B10) | Building 10 | Return loop (B10) | PW | 2026-03-21 | 2026-03-24 | 0 | 0 | 0 |  | 100 | PASSED | FALSE | WT-26-0038 | complete | pending
2026-03-20 | OSD13 | DV116.25 | PQ3-Week3 | TRUE | 10-3-171 | Building 10 | TOOL WASHING-P | PW | 2026-03-21 | 2026-03-24 | 0 | 0 | 0 |  | 100 | PASSED | FALSE | WT-26-0038 | complete | pending
2026-03-20 | OSD14 | DV116.24 | PQ3-Week3 | TRUE | 10-3-163 | Building 10 | WET GRANULATION 1-P | PW | 2026-03-21 | 2026-03-24 | 0 | 0 | 0 |  | 100 | PASSED | FALSE | WT-26-0038 | complete | pending
2026-03-20 | OSD15 | DV116.23 | PQ3-Week3 | TRUE | 10-3-159 | Building 10 | BINDER PREPARATION-P | PW | 2026-03-21 | 2026-03-24 | 0 | 0 | 0 |  | 100 | PASSED | FALSE | WT-26-0038 | complete | pending
2026-03-20 | OSD16 | DV116.21 | PQ3-Week3 | TRUE | 10-3-152 | Building 10 | WASHING-P | PW | 2026-03-21 | 2026-03-24 | 0 | 0 | 0 |  | 100 | PASSED | FALSE | WT-26-0038 | complete | pending
2026-03-20 | OSD17 | DV116.22 | PQ3-Week3 | TRUE | 10-3-152 | Building 10 | WASHING-P | PW | 2026-03-21 | 2026-03-24 | 0 | 0 | 0 |  | 100 | PASSED | FALSE | WT-26-0038 | complete | pending
2026-03-20 | OSD18 | SV116.13 | PQ3-Week3 | TRUE | 10-3-152 | Building 10 | WASHING-P | PW | 2026-03-21 | 2026-03-24 | 0 | 0 | 0 |  | 100 | PASSED | FALSE | WT-26-0038 | complete | pending
2026-03-20 | OSD19 | DV116.20 | PQ3-Week3 | TRUE | 10-3-149 | Building 10 | IPQC-1-P | PW | 2026-03-21 | 2026-03-24 | 0 | 0 | 0 |  | 100 | PASSED | FALSE | WT-26-0038 | complete | pending
2026-03-20 | OSD20 | DV116.19 | PQ3-Week3 | TRUE | 10-3-143 | Building 10 | COATING SOLUTION PREP.-P | PW | 2026-03-21 | 2026-03-24 | 0 | 0 | 0 |  | 100 | PASSED | FALSE | WT-26-0038 | complete | pending
2026-03-20 | OSD21 | SV116.12 | PQ3-Week3 | TRUE | 10-3-144 | Building 10 | COATING-P | PW | 2026-03-21 | 2026-03-24 | 0 | 0 | 0 |  | 100 | PASSED | FALSE | WT-26-0038 | complete | pending
2026-03-20 | OSD41 | DV116.02 | PQ3-Week3 | TRUE | 10-1-115 | Building 10 | WASHING | PW | 2026-03-21 | 2026-03-24 | 0 | 0 | 0 |  | 100 | PASSED | FALSE | WT-26-0038 | complete | pending
2026-03-20 | OSD42 | DV116.01 | PQ3-Week3 | TRUE | 10-1-057 | Building 10 | WASHING-P | PW | 2026-03-21 | 2026-03-24 | 0 | 0 | 0 |  | 100 | PASSED | FALSE | WT-26-0038 | complete | pending
2026-03-24 | GOCL05 | SV123.01 | PQ3-Week4 | TRUE | WATER SYSTEM (B16) | Building 16 | After Storage tank (B16) | PW | 2026-03-25 | 2026-03-29 | 0 | 0 | 0 |  | 100 | PASSED | FALSE | WT-26-0039 | complete | pending
2026-03-24 | GOCL07 | SV125.02 | PQ3-Week4 | TRUE | WATER SYSTEM (B16) | Building 16 | After UV (B16) | PW | 2026-03-25 | 2026-03-29 | 50 | 54 | 52 |  | 100 | PASSED | FALSE | WT-26-0039 | complete | pending
2026-03-24 | GOCL08 | SV127.01 | PQ3-Week4 | TRUE | WATER SYSTEM (B16) | Building 16 | Return loop (B16) | PW | 2026-03-25 | 2026-03-29 | 0 | 0 | 0 |  | 100 | PASSED | FALSE | WT-26-0039 | complete | pending
2026-03-24 | OCL09 | DV126.10 | PQ3-Week4 | TRUE | 16-3-069 | Building 16 | MFG 2 | PW | 2026-03-25 | 2026-03-29 | 0 | 0 | 0 |  | 100 | PASSED | FALSE | WT-26-0039 | complete | pending
2026-03-24 | OCL10 | DV126.06 | PQ3-Week4 | TRUE | 16-3-069 | Building 16 | MFG 2 | PW | 2026-03-25 | 2026-03-29 | 0 | 0 | 0 |  | 100 | PASSED | FALSE | WT-26-0039 | complete | pending
2026-03-24 | OCL11 | SV126.10 | PQ3-Week4 | TRUE | 16-3-071 | Building 16 | MFG 3 (1200L) | PW | 2026-03-25 | 2026-03-29 | 0 | 0 | 0 |  | 100 | PASSED | FALSE | WT-26-0039 | complete | pending
2026-03-24 | OCL12 | SV126.09 | PQ3-Week4 | TRUE | 16-3-071 | Building 16 | MFG 3 (5000L) | PW | 2026-03-25 | 2026-03-29 | 0 | 0 | 0 |  | 100 | PASSED | FALSE | WT-26-0039 | complete | pending
2026-03-24 | OCL18 | DV126.08 | PQ3-Week4 | TRUE | 16-3-077 | Building 16 | MFG 6 | PW | 2026-03-25 | 2026-03-29 | 0 | 0 | 0 |  | 100 | PASSED | FALSE | WT-26-0039 | complete | pending
2026-03-24 | OCL19 | DV126.07 | PQ3-Week4 | TRUE | 16-3-077 | Building 16 | MFG 6 | PW | 2026-03-25 | 2026-03-29 | 0 | 0 | 0 |  | 100 | PASSED | FALSE | WT-26-0039 | complete | pending
2026-03-24 | OCL15 | SV126.14 | PQ3-Week4 | TRUE | 16-3-073 | Building 16 | MFG 4 (400L) | PW | 2026-03-25 | 2026-03-29 | 0 | 0 | 0 |  | 100 | PASSED | FALSE | WT-26-0039 | complete | pending
2026-03-24 | GOLD05 | SV133.01 | PQ3-Week4 | TRUE | WATER SYSTEM (B12) | Building 12 | After Storage tank (B12) | PW | 2026-03-25 | 2026-03-29 | 0 | 0 | 0 |  | 100 | PASSED | FALSE | WT-26-0040 | complete | pending
2026-03-24 | GOLD06 | SV135.02 | PQ3-Week4 | TRUE | WATER SYSTEM (B12) | Building 12 | After UV (B12) | PW | 2026-03-25 | 2026-03-29 | 0 | 0 | 0 |  | 100 | PASSED | FALSE | WT-26-0040 | complete | pending
2026-03-24 | GOLD07 | SV137.01 | PQ3-Week4 | TRUE | WATER SYSTEM (B12) | Building 12 | Return loop (B12) | PW | 2026-03-25 | 2026-03-29 | 0 | 0 | 0 |  | 100 | PASSED | FALSE | WT-26-0040 | complete | pending
2026-03-24 | OLD06 | SV136.09 | PQ3-Week4 | TRUE | 12-2-039 | Building 12 | MFG 1 | PW | 2026-03-25 | 2026-03-29 | 0 | 0 | 0 |  | 100 | PASSED | FALSE | WT-26-0040 | complete | pending
2026-03-24 | OLD07 | SV136.10 | PQ3-Week4 | TRUE | 12-2-041 | Building 12 | MFG 2 | PW | 2026-03-25 | 2026-03-29 | 0 | 0 | 0 |  | 100 | PASSED | FALSE | WT-26-0040 | complete | pending
2026-03-24 | OLD08 | SV136.11 | PQ3-Week4 | TRUE | 12-2-043 | Building 12 | MFG 3 | PW | 2026-03-25 | 2026-03-29 | 0 | 0 | 0 |  | 100 | PASSED | FALSE | WT-26-0040 | complete | pending
2026-03-24 | OLD09 | SV136.13 | PQ3-Week4 | TRUE | 12-2-043 | Building 12 | MFG 3 | PW | 2026-03-25 | 2026-03-29 | 0 | 0 | 0 |  | 100 | PASSED | FALSE | WT-26-0040 | complete | pending
2026-03-24 | OLD11 | SV136.08 | PQ3-Week4 | TRUE | 12-2-043 | Building 12 | MFG 3 | PW | 2026-03-25 | 2026-03-29 | 0 | 0 | 0 |  | 100 | PASSED | FALSE | WT-26-0040 | complete | pending
2026-03-24 | OLD16 | SV136.14 | PQ3-Week4 | TRUE | 12-2-045 | Building 12 | MFG 4 | PW | 2026-03-25 | 2026-03-29 | 0 | 0 | 0 |  | 100 | PASSED | FALSE | WT-26-0040 | complete | pending
2026-03-24 | OLD18 | SV136.02 | PQ3-Week4 | TRUE | 12-2-024 | Building 12 | LIQUORICE EXTRACT | PW | 2026-03-25 | 2026-03-29 | 0 | 0 | 0 |  | 100 | PASSED | FALSE | WT-26-0040 | complete | pending
2026-03-24 | OLD32 | DV136.08 | PQ3-Week4 | TRUE | 12-3-042 | Building 12 | SAMPLE PREPARATION | PW | 2026-03-25 | 2026-03-29 | 26 | 27 | 27 |  | 100 | PASSED | FALSE | WT-26-0040 | complete | pending
2026-03-24 | OLD33 | DV136.09 | PQ3-Week4 | TRUE | 12-3-042 | Building 12 | SAMPLE PREPARATION | PW | 2026-03-25 | 2026-03-29 | 36 | 16 | 26 |  | 100 | PASSED | FALSE | WT-26-0040 | complete | pending
2026-03-27 | GOSD06 | SV113.01 | PQ3-Week4 | TRUE | WATER SYSTEM (B10) | Building 10 | After Storage tank (B10) | PW | 2026-03-28 | 2026-03-31 | 0 | 0 | 0 |  | 100 | PASSED | FALSE | WT-26-0041 | complete | pending
2026-03-27 | GOSD07 | SV115.02 | PQ3-Week4 | TRUE | WATER SYSTEM (B10) | Building 10 | After UV (B10) | PW | 2026-03-28 | 2026-03-31 | 0 | 0 | 0 |  | 100 | PASSED | FALSE | WT-26-0041 | complete | pending
2026-03-27 | GOSD08 | SV117.01 | PQ3-Week4 | TRUE | WATER SYSTEM (B10) | Building 10 | Return loop (B10) | PW | 2026-03-28 | 2026-03-31 | 0 | 0 | 0 |  | 100 | PASSED | FALSE | WT-26-0041 | complete | pending
2026-03-27 | OSD01 | SV116.15 | PQ3-Week4 | TRUE | 10-4-012 | Building 10 | CIP SKID-1 FOR BIN WASHING-1 | PW | 2026-03-28 | 2026-03-31 | 0 | 0 | 0 |  | 100 | PASSED | FALSE | WT-26-0041 | complete | pending
2026-03-27 | OSD02 | SV116.16 | PQ3-Week4 | TRUE | 10-4-012 | Building 10 | WIP SKID-3 FOR GRANULATION POTENT | PW | 2026-03-28 | 2026-03-31 | 0 | 0 | 0 |  | 100 | PASSED | FALSE | WT-26-0041 | complete | pending
2026-03-27 | OSD03 | SV116.17 | PQ3-Week4 | TRUE | 10-4-012 | Building 10 | CIP SKID-2 FOR BIN WASHING-1 | PW | 2026-03-28 | 2026-03-31 | 0 | 0 | 0 |  | 100 | PASSED | FALSE | WT-26-0041 | complete | pending
2026-03-27 | OSD04 | SV116.18 | PQ3-Week4 | TRUE | 10-4-012 | Building 10 | WIP SKID-1 FOR GRANULATION NON POTENT | PW | 2026-03-28 | 2026-03-31 | 0 | 0 | 0 |  | 100 | PASSED | FALSE | WT-26-0041 | complete | pending
2026-03-27 | OSD05 | SV116.19 | PQ3-Week4 | TRUE | 10-4-012 | Building 10 | WIP SKID-2 FOR GRANULATION NON POTENT | PW | 2026-03-28 | 2026-03-31 | 0 | 0 | 0 |  | 100 | PASSED | FALSE | WT-26-0041 | complete | pending
2026-03-27 | OSD34 | SV116.02 | PQ3-Week4 | TRUE | 10-2-037 | Building 10 | SKID FOR BIN WASHING-2 | PW | 2026-03-28 | 2026-03-31 | 0 | 0 | 0 |  | 100 | PASSED | FALSE | WT-26-0041 | complete | pending
2026-03-27 | OSD35 | SV116.01 | PQ3-Week4 | TRUE | 10-2-021 | Building 10 | INSTRUMENT-1 | PW | 2026-03-28 | 2026-03-31 | 0 | 0 | 0 |  | 100 | PASSED | FALSE | WT-26-0041 | complete | pending
2026-03-27 | OSD43 | DV116.26 | PQ3-Week4 | TRUE | 10-4-015 | Building 10 | WATER SYSTEM ROOM | PW | 2026-03-28 | 2026-03-31 | 0 | 0 | 0 |  | 100 | PASSED | FALSE | WT-26-0041 | complete | pending
2026-04-03 | BU19-14 | SV-14 | PQ3-Week1 | TRUE | PROCESS WATER (B19) | Building 19 | AFTER RO SYSTEM NO.12 SV14 | PRW | 2026-04-04 | 2026-04-08 | 0 | 0 | 0 |  | 500 | PASSED | FALSE | WT-26-0045 | complete | pending
2026-04-03 | GOSD01 | VB-05(10) | PQ3-Week1 | TRUE | WATER SYSTEM (B10) | Building 10 | After Chlorine circulation tank (B10) | PRW | 2026-04-04 | 2026-04-08 | 0 | 0 | 0 |  | 500 | PASSED | FALSE | WT-26-0046 | complete | pending
2026-04-03 | GOSD03 | V50-61(10) | PQ3-Week1 | TRUE | WATER SYSTEM (B10) | Building 10 | After Cartridge filter 5 µm (B10) | PRW | 2026-04-04 | 2026-04-08 | 0 | 0 | 0 |  | 500 | PASSED | FALSE | WT-26-0046 | complete | pending
2026-04-03 | GOSD04 | V50-11C(10) | PQ3-Week1 | TRUE | WATER SYSTEM (B10) | Building 10 | After RO (Before EDI) (B10) | RO water | 2026-04-04 | 2026-04-08 | 0 | 0 | 0 |  | 500 | PASSED | FALSE | WT-26-0046 | complete | pending
2026-04-03 | GOSD05 | V50-39(10) | PQ3-Week1 | TRUE | WATER SYSTEM (B10) | Building 10 | After EDI (B10) | PW | 2026-04-04 | 2026-04-08 | 0 | 0 | 0 |  | 100 | PASSED | FALSE | WT-26-0046 | complete | pending
2026-04-03 | GOSD08 | SV117.01 | PQ3-Week1 | TRUE | WATER SYSTEM (B10) | Building 10 | Return loop (B10) | PW | 2026-04-04 | 2026-04-08 | 0 | 0 | 0 |  | 100 | PASSED | FALSE | WT-26-0046 | complete | pending
2026-04-03 | OSD06 | DV116.18 | PQ3-Week1 | TRUE | 10-3-111 | Building 10 | WET GRANULATION-5 | PW | 2026-04-04 | 2026-04-08 | 0 | 0 | 0 |  | 100 | PASSED | FALSE | WT-26-0046 | complete | pending
2026-04-03 | OSD07 | DV116.16 | PQ3-Week1 | TRUE | 10-3-107 | Building 10 | WET GRANULATION-2 | PW | 2026-04-04 | 2026-04-08 | 0 | 0 | 0 |  | 100 | PASSED | FALSE | WT-26-0046 | complete | pending
2026-04-03 | OSD08 | SV116.11 | PQ3-Week1 | TRUE | 10-3-107 | Building 10 | WET GRANULATION-2 | PW | 2026-04-04 | 2026-04-08 | 0 | 0 | 0 |  | 100 | PASSED | FALSE | WT-26-0046 | complete | pending
2026-04-03 | OSD09 | DV116.14 | PQ3-Week1 | TRUE | 10-3-086 | Building 10 | TOOL WASHING | PW | 2026-04-04 | 2026-04-08 | 0 | 0 | 0 |  | 100 | PASSED | FALSE | WT-26-0046 | complete | pending
2026-04-03 | OSD10 | SV116.09 | PQ3-Week1 | TRUE | 10-3-078 | Building 10 | WASHING | PW | 2026-04-04 | 2026-04-08 | 0 | 0 | 0 |  | 100 | PASSED | FALSE | WT-26-0046 | complete | pending
2026-04-03 | OSD11 | DV116.13 | PQ3-Week1 | TRUE | 10-3-078 | Building 10 | WASHING | PW | 2026-04-04 | 2026-04-08 | 0 | 0 | 0 |  | 100 | PASSED | FALSE | WT-26-0046 | complete | pending
2026-04-03 | OSD12 | DV116.12 | PQ3-Week1 | TRUE | 10-3-078 | Building 10 | WASHING | PW | 2026-04-04 | 2026-04-08 | 0 | 0 | 0 |  | 100 | PASSED | FALSE | WT-26-0046 | complete | pending
2026-04-03 | OSD22 | SV116.05 | PQ3-Week1 | TRUE | 10-3-062 | Building 10 | COATING ROOM-3 | PW | 2026-04-04 | 2026-04-08 | 0 | 0 | 0 |  | 100 | PASSED | FALSE | WT-26-0046 | complete | pending
2026-04-03 | OSD23 | SV116.04 | PQ3-Week1 | TRUE | 10-3-061 | Building 10 | COATING ROOM-2 | PW | 2026-04-04 | 2026-04-08 | 0 | 0 | 0 |  | 100 | PASSED | FALSE | WT-26-0046 | complete | pending
2026-04-03 | OSD24 | DV116.09 | PQ3-Week1 | TRUE | 10-3-060 | Building 10 | COATING SOLUTION PREP.-2 | PW | 2026-04-04 | 2026-04-08 | 0 | 0 | 0 |  | 100 | PASSED | FALSE | WT-26-0046 | complete | pending
2026-04-03 | OSD25 | DV116.08 | PQ3-Week1 | TRUE | 10-3-059 | Building 10 | COATING SOLUTION PREP.-1 | PW | 2026-04-04 | 2026-04-08 | 0 | 0 | 0 |  | 100 | PASSED | FALSE | WT-26-0046 | complete | pending
2026-04-03 | OSD26 | SV116.03 | PQ3-Week1 | TRUE | 10-3-058 | Building 10 | COATING ROOM-1 | PW | 2026-04-04 | 2026-04-08 | 0 | 0 | 0 |  | 100 | PASSED | FALSE | WT-26-0046 | complete | pending
2026-04-03 | OSD27 | DV116.17 | PQ3-Week1 | TRUE | 10-3-117 | Building 10 | IPQC-2 | PW | 2026-04-04 | 2026-04-08 | 0 | 0 | 0 |  | 100 | PASSED | FALSE | WT-26-0046 | complete | pending
2026-04-03 | OSD28 | DV116.15 | PQ3-Week1 | TRUE | 10-3-104 | Building 10 | BINDER PREPARATION | PW | 2026-04-04 | 2026-04-08 | 0 | 0 | 0 |  | 100 | PASSED | FALSE | WT-26-0046 | complete | pending
2026-04-03 | GOLD07 | SV137.01 | PQ3-Week1 | TRUE | WATER SYSTEM (B12) | Building 12 | Return loop (B12) | PW | 2026-04-04 | 2026-04-08 | 0 | 0 | 0 |  | 100 | PASSED | FALSE | WT-26-0047 | complete | pending
2026-04-03 | GOCL08 | SV127.01 | PQ3-Week1 | TRUE | WATER SYSTEM (B16) | Building 16 | Return loop (B16) | PW | 2026-04-04 | 2026-04-08 | 0 | 0 | 0 |  | 100 | PASSED | FALSE | WT-26-0048 | complete | pending
2026-04-07 | GOLD02 | V50-61 (12) | PQ3-Week2 | TRUE | WATER SYSTEM (B12) | Building 12 | After Cartridge filter 5 µm (B12) | PRW | 2026-04-08 | 2026-04-11 | 71 | 59 | 65 |  | 500 | PASSED | FALSE | WT-26-0049 | complete | pending
2026-04-07 | GOLD03 | V50-11C (12) | PQ3-Week2 | TRUE | WATER SYSTEM (B12) | Building 12 | After RO (Before EDI) (B12) | RO water | 2026-04-08 | 2026-04-11 | 0 | 0 | 0 |  | 500 | PASSED | FALSE | WT-26-0049 | complete | pending
2026-04-07 | GOLD04 | V50-39 (12) | PQ3-Week2 | TRUE | WATER SYSTEM (B12) | Building 12 | After EDI (B12) | PW | 2026-04-08 | 2026-04-11 | 0 | 0 | 0 |  | 100 | PASSED | FALSE | WT-26-0049 | complete | pending
2026-04-07 | GOLD05 | SV133.01 | PQ3-Week2 | TRUE | WATER SYSTEM (B12) | Building 12 | After Storage tank (B12) | PW | 2026-04-08 | 2026-04-11 | 0 | 0 | 0 |  | 100 | PASSED | FALSE | WT-26-0049 | complete | pending
2026-04-07 | GOLD06 | SV135.02 | PQ3-Week2 | TRUE | WATER SYSTEM (B12) | Building 12 | After UV (B12) | PW | 2026-04-08 | 2026-04-11 | 0 | 0 | 0 |  | 100 | PASSED | FALSE | WT-26-0049 | complete | pending
2026-04-07 | GOLD07 | SV137.01 | PQ3-Week2 | TRUE | WATER SYSTEM (B12) | Building 12 | Return loop (B12) | PW | 2026-04-08 | 2026-04-11 | 0 | 0 | 0 |  | 100 | PASSED | FALSE | WT-26-0049 | complete | pending
2026-04-07 | OLD21 | DV136.15 | PQ3-Week2 | TRUE | 12-3-078 | Building 12 | GLASSWARE WASHING 2 | PW | 2026-04-08 | 2026-04-11 | 0 | 0 | 0 |  | 100 | PASSED | FALSE | WT-26-0049 | complete | pending
2026-04-07 | OLD22 | DV136.13 | PQ3-Week2 | TRUE | 12-3-057 | Building 12 | STERILIZATION | PW | 2026-04-08 | 2026-04-11 | 0 | 0 | 0 |  | 100 | PASSED | FALSE | WT-26-0049 | complete | pending
2026-04-07 | OLD23 | SV136.18 | PQ3-Week2 | TRUE | 12-3-059 | Building 12 | AUTOCLAVE | PW | 2026-04-08 | 2026-04-11 | 0 | 0 | 0 |  | 100 | PASSED | FALSE | WT-26-0049 | complete | pending
2026-04-07 | OLD24 | DV136.11 | PQ3-Week2 | TRUE | 12-3-059 | Building 12 | AUTOCLAVE | PW | 2026-04-08 | 2026-04-11 | 0 | 0 | 0 |  | 100 | PASSED | FALSE | WT-26-0049 | complete | pending
2026-04-07 | OLD25 | DV136.12 | PQ3-Week2 | TRUE | 12-3-056 | Building 12 | MEDIA PREPARATION | PW | 2026-04-08 | 2026-04-11 | 0 | 0 | 0 |  | 100 | PASSED | FALSE | WT-26-0049 | complete | pending
2026-04-07 | OLD26 | DV136.10 | PQ3-Week2 | TRUE | 12-3-056 | Building 12 | MEDIA PREPARATION | PW | 2026-04-08 | 2026-04-11 | 0 | 0 | 0 |  | 100 | PASSED | FALSE | WT-26-0049 | complete | pending
2026-04-07 | OLD27 | DV136.14 | PQ3-Week2 | TRUE | 12-3-074 | Building 12 | DECONTAMINATION | PW | 2026-04-08 | 2026-04-11 | 0 | 0 | 0 |  | 100 | PASSED | FALSE | WT-26-0049 | complete | pending
2026-04-07 | OLD28 | DV136.18 | PQ3-Week2 | TRUE | 12-3-037 | Building 12 | GLASSWARE WASHING 1 | PW | 2026-04-08 | 2026-04-11 | 0 | 0 | 0 |  | 100 | PASSED | FALSE | WT-26-0049 | complete | pending
2026-04-07 | OLD29 | DV136.05 | PQ3-Week2 | TRUE | 12-3-037 | Building 12 | GLASSWARE WASHING 1 | PW | 2026-04-08 | 2026-04-11 | 0 | 0 | 0 |  | 100 | PASSED | FALSE | WT-26-0049 | complete | pending
2026-04-07 | OLD30 | DV136.06 | PQ3-Week2 | TRUE | 12-3-037 | Building 12 | GLASSWARE WASHING 1 | PW | 2026-04-08 | 2026-04-11 | 0 | 0 | 0 |  | 100 | PASSED | FALSE | WT-26-0049 | complete | pending
2026-04-07 | OLD31 | DV136.07 | PQ3-Week2 | TRUE | 12-3-039 | Building 12 | INSTRUMENT 7 | PW | 2026-04-08 | 2026-04-11 | 0 | 0 | 0 |  | 100 | PASSED | FALSE | WT-26-0049 | complete | pending
2026-04-07 | OLD32 | DV136.08 | PQ3-Week2 | TRUE | 12-3-042 | Building 12 | SAMPLE PREPARATION | PW | 2026-04-08 | 2026-04-11 | 0 | 0 | 0 |  | 100 | PASSED | FALSE | WT-26-0049 | complete | pending
2026-04-07 | OLD33 | DV136.09 | PQ3-Week2 | TRUE | 12-3-042 | Building 12 | SAMPLE PREPARATION | PW | 2026-04-08 | 2026-04-11 | 15 | 18 | 17 |  | 100 | PASSED | FALSE | WT-26-0049 | complete | pending
2026-04-07 | GOCL01 | VB-05 (16) | PQ3-Week2 | TRUE | WATER SYSTEM (B16) | Building 16 | After Chlorine circulation tank (B16) | PRW | 2026-04-08 | 2026-04-11 | 0 | 0 | 0 |  | 500 | PASSED | FALSE | WT-26-0050 | complete | pending
2026-04-07 | GOCL02 | V50-61 (16) | PQ3-Week2 | TRUE | WATER SYSTEM (B16) | Building 16 | After Cartridge filter 5 µm (B16) | PRW | 2026-04-08 | 2026-04-11 | 60 | 69 | 65 |  | 500 | PASSED | FALSE | WT-26-0050 | complete | pending
2026-04-07 | GOCL03 | V50-11C (16) | PQ3-Week2 | TRUE | WATER SYSTEM (B16) | Building 16 | After RO (Before EDI) (B16) | RO water | 2026-04-08 | 2026-04-11 | 0 | 0 | 0 |  | 500 | PASSED | FALSE | WT-26-0050 | complete | pending
2026-04-07 | GOCL04 | V50-39 (16) | PQ3-Week2 | TRUE | WATER SYSTEM (B16) | Building 16 | After EDI (B16) | PW | 2026-04-08 | 2026-04-11 | 0 | 0 | 0 |  | 100 | PASSED | FALSE | WT-26-0050 | complete | pending
2026-04-07 | GOCL05 | SV123.01 | PQ3-Week2 | TRUE | WATER SYSTEM (B16) | Building 16 | After Storage tank (B16) | PW | 2026-04-08 | 2026-04-11 | 0 | 0 | 0 |  | 100 | PASSED | FALSE | WT-26-0050 | complete | pending
2026-04-07 | GOCL07 | SV125.02 | PQ3-Week2 | TRUE | WATER SYSTEM (B16) | Building 16 | After UV (B16) | PW | 2026-04-08 | 2026-04-11 | 0 | 0 | 0 |  | 100 | PASSED | FALSE | WT-26-0050 | complete | pending
2026-04-07 | GOCL08 | SV127.01 | PQ3-Week2 | TRUE | WATER SYSTEM (B16) | Building 16 | Return loop (B16) | PW | 2026-04-08 | 2026-04-11 | 0 | 0 | 0 |  | 100 | PASSED | FALSE | WT-26-0050 | complete | pending
2026-04-07 | OCL01 | DV126.02 | PQ3-Week2 | TRUE | 16-1-082 | Building 16 | WASHING | PW | 2026-04-08 | 2026-04-11 | 0 | 0 | 0 |  | 100 | PASSED | FALSE | WT-26-0050 | complete | pending
2026-04-07 | OCL02 | DV126.01 | PQ3-Week2 | TRUE | 16-1-082 | Building 16 | WASHING | PW | 2026-04-08 | 2026-04-11 | 0 | 0 | 0 |  | 100 | PASSED | FALSE | WT-26-0050 | complete | pending
2026-04-07 | OCL03 | SV126.02 | PQ3-Week2 | TRUE | 16-1-098 | Building 16 | CIP/SIP (EQUIPMENT REQUIREMENT – 200L) | PW | 2026-04-08 | 2026-04-11 | 0 | 0 | 0 |  | 100 | PASSED | FALSE | WT-26-0050 | complete | pending
2026-04-07 | OCL04 | DV126.03 | PQ3-Week2 | TRUE | 16-1-098 | Building 16 | CIP/SIP (SINK WASHING) | PW | 2026-04-08 | 2026-04-11 | 0 | 0 | 0 |  | 100 | PASSED | FALSE | WT-26-0050 | complete | pending
2026-04-07 | OCL05 | SV126.01 | PQ3-Week2 | TRUE | 16-1-092 | Building 16 | LINEN WASHING | PW | 2026-04-08 | 2026-04-11 | 0 | 0 | 0 |  | 100 | PASSED | FALSE | WT-26-0050 | complete | pending
2026-04-07 | OCL09 | DV126.10 | PQ3-Week2 | TRUE | 16-3-069 | Building 16 | MFG 2 | PW | 2026-04-08 | 2026-04-11 | 0 | 0 | 0 |  | 100 | PASSED | FALSE | WT-26-0050 | complete | pending
2026-04-07 | OCL10 | DV126.06 | PQ3-Week2 | TRUE | 16-3-069 | Building 16 | MFG 2 | PW | 2026-04-08 | 2026-04-11 | 0 | 0 | 0 |  | 100 | PASSED | FALSE | WT-26-0050 | complete | pending
2026-04-07 | OCL21 | DV126.05 | PQ3-Week2 | TRUE | 16-3-054 | Building 16 | WASHING | PW | 2026-04-08 | 2026-04-11 | 0 | 0 | 0 |  | 100 | PASSED | FALSE | WT-26-0050 | complete | pending
2026-04-10 | GOSD06 | SV113.01 | PQ3-Week2 | TRUE | WATER SYSTEM (B10) | Building 10 | After Storage tank (B10) | PW | 2026-04-11 | 2026-04-15 | 0 | 0 | 0 |  | 100 | PASSED | FALSE | WT-26-0076 | complete | synced
2026-04-10 | GOSD07 | SV115.02 | PQ3-Week2 | TRUE | WATER SYSTEM (B10) | Building 10 | After UV (B10) | PW | 2026-04-11 | 2026-04-15 | 0 | 0 | 0 |  | 100 | PASSED | FALSE | WT-26-0076 | complete | synced
2026-04-10 | GOSD08 | SV117.01 | PQ3-Week2 | TRUE | WATER SYSTEM (B10) | Building 10 | Return loop (B10) | PW | 2026-04-11 | 2026-04-15 | 0 | 0 | 0 |  | 100 | PASSED | FALSE | WT-26-0076 | complete | synced
2026-04-10 | OSD13 | DV116.25 | PQ3-Week2 | TRUE | 10-3-171 | Building 10 | TOOL WASHING-P | PW | 2026-04-11 | 2026-04-15 | 0 | 0 | 0 |  | 100 | PASSED | FALSE | WT-26-0076 | complete | synced
2026-04-10 | OSD14 | DV116.24 | PQ3-Week2 | TRUE | 10-3-163 | Building 10 | WET GRANULATION 1-P | PW | 2026-04-11 | 2026-04-15 | 0 | 0 | 0 |  | 100 | PASSED | FALSE | WT-26-0076 | complete | synced
2026-04-10 | OSD15 | DV116.23 | PQ3-Week2 | TRUE | 10-3-159 | Building 10 | BINDER PREPARATION-P | PW | 2026-04-11 | 2026-04-15 | 0 | 0 | 0 |  | 100 | PASSED | FALSE | WT-26-0076 | complete | synced
2026-04-10 | OSD16 | DV116.21 | PQ3-Week2 | TRUE | 10-3-152 | Building 10 | WASHING-P | PW | 2026-04-11 | 2026-04-15 | 0 | 0 | 0 |  | 100 | PASSED | FALSE | WT-26-0076 | complete | synced
2026-04-10 | OSD17 | DV116.22 | PQ3-Week2 | TRUE | 10-3-152 | Building 10 | WASHING-P | PW | 2026-04-11 | 2026-04-15 | 0 | 0 | 0 |  | 100 | PASSED | FALSE | WT-26-0076 | complete | synced
2026-04-10 | OSD18 | SV116.13 | PQ3-Week2 | TRUE | 10-3-152 | Building 10 | WASHING-P | PW | 2026-04-11 | 2026-04-15 | 0 | 0 | 0 |  | 100 | PASSED | FALSE | WT-26-0076 | complete | synced
2026-04-10 | OSD19 | DV116.20 | PQ3-Week2 | TRUE | 10-3-149 | Building 10 | IPQC-1-P | PW | 2026-04-11 | 2026-04-15 | 0 | 0 | 0 |  | 100 | PASSED | FALSE | WT-26-0076 | complete | synced
2026-04-10 | OSD20 | DV116.19 | PQ3-Week2 | TRUE | 10-3-143 | Building 10 | COATING SOLUTION PREP.-P | PW | 2026-04-11 | 2026-04-15 | 0 | 0 | 0 |  | 100 | PASSED | FALSE | WT-26-0076 | complete | synced
2026-04-10 | OSD21 | SV116.12 | PQ3-Week2 | TRUE | 10-3-144 | Building 10 | COATING-P | PW | 2026-04-11 | 2026-04-15 | 0 | 0 | 0 |  | 100 | PASSED | FALSE | WT-26-0076 | complete | synced
2026-04-10 | OSD29 | SV116.08 | PQ3-Week2 | TRUE | 10-3-067 | Building 10 | COATING ROOM-6 | PW | 2026-04-11 | 2026-04-15 | 0 | 0 | 0 |  | 100 | PASSED | FALSE | WT-26-0076 | complete | synced
2026-04-10 | OSD30 | DV116.11 | PQ3-Week2 | TRUE | 10-3-066 | Building 10 | COATING SOLUTION PREP.-4 | PW | 2026-04-11 | 2026-04-15 | 0 | 0 | 0 |  | 100 | PASSED | FALSE | WT-26-0076 | complete | synced
2026-04-10 | OSD31 | DV116.10 | PQ3-Week2 | TRUE | 10-3-065 | Building 10 | COATING SOLUTION PREP.-3 | PW | 2026-04-11 | 2026-04-15 | 0 | 0 | 0 |  | 100 | PASSED | FALSE | WT-26-0076 | complete | synced
2026-04-10 | OSD32 | SV116.07 | PQ3-Week2 | TRUE | 10-3-064 | Building 10 | COATING ROOM-5 | PW | 2026-04-11 | 2026-04-15 | 0 | 0 | 0 |  | 100 | PASSED | FALSE | WT-26-0076 | complete | synced
2026-04-10 | OSD33 | SV116.06 | PQ3-Week2 | TRUE | 10-3-063 | Building 10 | COATING ROOM-4 | PW | 2026-04-11 | 2026-04-15 | 0 | 0 | 0 |  | 100 | PASSED | FALSE | WT-26-0076 | complete | synced
2026-04-10 | OSD41 | DV116.02 | PQ3-Week2 | TRUE | 10-1-115 | Building 10 | WASHING | PW | 2026-04-11 | 2026-04-15 | 0 | 0 | 0 |  | 100 | PASSED | FALSE | WT-26-0076 | complete | synced
2026-04-10 | OSD42 | DV116.01 | PQ3-Week2 | TRUE | 10-1-057 | Building 10 | WASHING-P | PW | 2026-04-11 | 2026-04-15 | 3 | 0 | 2 |  | 100 | PASSED | FALSE | WT-26-0076 | complete | synced
2026-04-10 | B11 | #N/A |  | TRUE | #N/A |  | #N/A | #N/A | 2026-04-11 | 2026-04-15 | 0 | 0 | 0 |  | #N/A | NA | FALSE | WT-26-0077 | complete | synced
2026-04-21 | GOCL01 | VB-05 (16) | PQ3-Week3 | TRUE | WATER SYSTEM (B16) | Building 16 | After Chlorine circulation tank (B16) | PRW | 2026-04-22 | 2026-04-25 | 0 | 0 | 0 |  | 500 | PASSED | FALSE | WT-26-0053 | complete | pending
2026-04-21 | GOCL02 | V50-61 (16) | PQ3-Week3 | TRUE | WATER SYSTEM (B16) | Building 16 | After Cartridge filter 5 µm (B16) | PRW | 2026-04-22 | 2026-04-25 | 321 | 340 | 331 |  | 500 | PASSED | FALSE | WT-26-0053 | complete | pending
2026-04-21 | GOCL03 | V50-11C (16) | PQ3-Week3 | TRUE | WATER SYSTEM (B16) | Building 16 | After RO (Before EDI) (B16) | RO water | 2026-04-22 | 2026-04-25 | 0 | 0 | 0 |  | 500 | PASSED | FALSE | WT-26-0053 | complete | pending
2026-04-21 | GOCL04 | V50-39 (16) | PQ3-Week3 | TRUE | WATER SYSTEM (B16) | Building 16 | After EDI (B16) | PW | 2026-04-22 | 2026-04-25 | 0 | 0 | 0 |  | 100 | PASSED | FALSE | WT-26-0053 | complete | pending
2026-04-21 | GOCL08 | SV127.01 | PQ3-Week3 | TRUE | WATER SYSTEM (B16) | Building 16 | Return loop (B16) | PW | 2026-04-22 | 2026-04-25 | 0 | 0 | 0 |  | 100 | PASSED | FALSE | WT-26-0053 | complete | pending
2026-04-21 | OCL06 | SV126.06 | PQ3-Week3 | TRUE | 16-3-067 | Building 16 | MFG 1 | PW | 2026-04-22 | 2026-04-25 | 0 | 0 | 0 |  | 100 | PASSED | FALSE | WT-26-0053 | complete | pending
2026-04-21 | OCL07 | SV126.21 | PQ3-Week3 | TRUE | 16-3-090 | Building 16 | CIP 1 (EQUIPMENT REQUIREMENT) | PW | 2026-04-22 | 2026-04-25 | 0 | 0 | 0 |  | 100 | PASSED | FALSE | WT-26-0053 | complete | pending
2026-04-21 | OCL08 | DV126.09 | PQ3-Week3 | TRUE | 16-3-090 | Building 16 | CIP 1 (ZINK WASHING) | PW | 2026-04-22 | 2026-04-25 | 0 | 0 | 0 |  | 100 | PASSED | FALSE | WT-26-0053 | complete | pending
2026-04-21 | OCL16 | SV126.18 | PQ3-Week3 | TRUE | 16-3-085 | Building 16 | CIP 3 (EQUIPMENT REQUIREMENT) | PW | 2026-04-22 | 2026-04-25 | 0 | 0 | 0 |  | 100 | PASSED | FALSE | WT-26-0053 | complete | pending
2026-04-21 | OCL18 | DV126.08 | PQ3-Week3 | TRUE | 16-3-077 | Building 16 | MFG 6 | PW | 2026-04-22 | 2026-04-25 | 0 | 0 | 0 |  | 100 | PASSED | FALSE | WT-26-0053 | complete | pending
2026-04-21 | OCL19 | DV126.07 | PQ3-Week3 | TRUE | 16-3-077 | Building 16 | MFG 6 | PW | 2026-04-22 | 2026-04-25 | 0 | 0 | 0 |  | 100 | PASSED | FALSE | WT-26-0053 | complete | pending
2026-04-21 | OCL20 | SV126.05 | PQ3-Week3 | TRUE | 16-3-049 | Building 16 | LINEN WASHING | PW | 2026-04-22 | 2026-04-25 | 0 | 0 | 0 |  | 100 | PASSED | FALSE | WT-26-0053 | complete | pending
2026-04-21 | OCL24 | DV126.04 | PQ3-Week3 | TRUE | 16-2-010 | Building 16 | WATER SYSTEM (PW) | PW | 2026-04-22 | 2026-04-25 | 0 | 0 | 0 |  | 100 | PASSED | FALSE | WT-26-0053 | complete | pending
2026-04-21 | GOLD02 | V50-61 (12) | PQ3-Week3 | TRUE | WATER SYSTEM (B12) | Building 12 | After Cartridge filter 5 µm (B12) | PRW | 2026-04-22 | 2026-04-25 | 76 | 77 | 77 |  | 500 | PASSED | FALSE | WT-26-0054 | complete | pending
2026-04-21 | GOLD03 | V50-11C (12) | PQ3-Week3 | TRUE | WATER SYSTEM (B12) | Building 12 | After RO (Before EDI) (B12) | RO water | 2026-04-22 | 2026-04-25 | 0 | 0 | 0 |  | 500 | PASSED | FALSE | WT-26-0054 | complete | pending
2026-04-21 | GOLD04 | V50-39 (12) | PQ3-Week3 | TRUE | WATER SYSTEM (B12) | Building 12 | After EDI (B12) | PW | 2026-04-22 | 2026-04-25 | 0 | 0 | 0 |  | 100 | PASSED | FALSE | WT-26-0054 | complete | pending
2026-04-21 | GOLD07 | SV137.01 | PQ3-Week3 | TRUE | WATER SYSTEM (B12) | Building 12 | Return loop (B12) | PW | 2026-04-22 | 2026-04-25 | 0 | 0 | 0 |  | 100 | PASSED | FALSE | WT-26-0054 | complete | pending
2026-04-21 | OLD01 | DV136.17 | PQ3-Week3 | TRUE | 12-2-065 | Building 12 | WASHING | PW | 2026-04-22 | 2026-04-25 | 11 | 4 | 8 |  | 100 | PASSED | FALSE | WT-26-0054 | complete | pending
2026-04-21 | OLD02 | SV136.16 | PQ3-Week3 | TRUE | 12-2-057 | Building 12 | CIP 2 | PW | 2026-04-22 | 2026-04-25 | 0 | 0 | 0 |  | 100 | PASSED | FALSE | WT-26-0054 | complete | pending
2026-04-21 | OLD06 | SV136.09 | PQ3-Week3 | TRUE | 12-2-039 | Building 12 | MFG 1 | PW | 2026-04-22 | 2026-04-25 | 0 | 0 | 0 |  | 100 | PASSED | FALSE | WT-26-0054 | complete | pending
2026-04-21 | OLD07 | SV136.10 | PQ3-Week3 | TRUE | 12-2-041 | Building 12 | MFG 2 | PW | 2026-04-22 | 2026-04-25 | 0 | 0 | 0 |  | 100 | PASSED | FALSE | WT-26-0054 | complete | pending
2026-04-21 | OLD10 | SV136.15 | PQ3-Week3 | TRUE | 12-2-055 | Building 12 | CIP 3 | PW | 2026-04-22 | 2026-04-25 | 0 | 0 | 0 |  | 100 | PASSED | FALSE | WT-26-0054 | complete | pending
2026-04-21 | OLD16 | SV136.14 | PQ3-Week3 | TRUE | 12-2-045 | Building 12 | MFG 4 | PW | 2026-04-22 | 2026-04-25 | 0 | 0 | 0 |  | 100 | PASSED | FALSE | WT-26-0054 | complete | pending
2026-04-21 | OLD17 | DV136.03 | PQ3-Week3 | TRUE | 12-2-053 | Building 12 | IPQC | PW | 2026-04-22 | 2026-04-25 | 0 | 0 | 0 |  | 100 | PASSED | FALSE | WT-26-0054 | complete | pending
2026-04-21 | OLD18 | SV136.02 | PQ3-Week3 | TRUE | 12-2-024 | Building 12 | LIQUORICE EXTRACT | PW | 2026-04-22 | 2026-04-25 | 0 | 0 | 0 |  | 100 | PASSED | FALSE | WT-26-0054 | complete | pending
2026-04-21 | OLD19 | DV136.01 | PQ3-Week3 | TRUE | 12-1-035 | Building 12 | SUGAR TRANSFERRING | PW | 2026-04-22 | 2026-04-25 | 0 | 0 | 0 |  | 100 | PASSED | FALSE | WT-26-0054 | complete | pending
2026-04-21 | OLD20 | DV136.16 | PQ3-Week3 | TRUE | 12-1-064 | Building 12 | WASHING | PW | 2026-04-22 | 2026-04-25 | 0 | 0 | 0 |  | 100 | PASSED | FALSE | WT-26-0054 | complete | pending
2026-04-21 | OLD34 | DV136.04 | PQ3-Week3 | TRUE | 12-2-077 | Building 12 | WATER SYSTEM ROOM | PW | 2026-04-22 | 2026-04-25 | 0 | 0 | 0 |  | 100 | PASSED | FALSE | WT-26-0054 | complete | pending
2026-04-24 | BU19-14 | SV-14 | PQ3-Week3 | TRUE | PROCESS WATER (B19) | #N/A | AFTER RO SYSTEM NO.12 SV14 | PRW | 2026-04-25 | 2026-04-29 | 181 | 141 | 161 |  | 500 | PASSED | FALSE | WT-26-0055 | complete | pending
2026-04-24 | GOSD01 | VB-05(10) | PQ3-Week3 | TRUE | WATER SYSTEM (B10) | Building 10 | After Chlorine circulation tank (B10) | PRW | 2026-04-25 | 2026-04-29 | 43 | 42 | 43 |  | 500 | PASSED | FALSE | WT-26-0056 | complete | pending
2026-04-24 | GOSD03 | V50-61(10) | PQ3-Week3 | TRUE | WATER SYSTEM (B10) | Building 10 | After Cartridge filter 5 µm (B10) | PRW | 2026-04-25 | 2026-04-29 | 4 | 0 | 2 |  | 500 | PASSED | FALSE | WT-26-0056 | complete | pending
2026-04-24 | GOSD04 | V50-11C(10) | PQ3-Week3 | TRUE | WATER SYSTEM (B10) | Building 10 | After RO (Before EDI) (B10) | RO water | 2026-04-25 | 2026-04-29 | 0 | 0 | 0 |  | 500 | PASSED | FALSE | WT-26-0056 | complete | pending
2026-04-24 | GOSD05 | V50-39(10) | PQ3-Week3 | TRUE | WATER SYSTEM (B10) | Building 10 | After EDI (B10) | PW | 2026-04-25 | 2026-04-29 | 0 | 0 | 0 |  | 100 | PASSED | FALSE | WT-26-0056 | complete | pending
2026-04-24 | GOSD06 | SV113.01 | PQ3-Week3 | TRUE | WATER SYSTEM (B10) | Building 10 | After Storage tank (B10) | PW | 2026-04-25 | 2026-04-29 | 0 | 0 | 0 |  | 100 | PASSED | FALSE | WT-26-0056 | complete | pending
2026-04-24 | GOSD07 | SV115.02 | PQ3-Week3 | TRUE | WATER SYSTEM (B10) | Building 10 | After UV (B10) | PW | 2026-04-25 | 2026-04-29 | 0 | 0 | 0 |  | 100 | PASSED | FALSE | WT-26-0056 | complete | pending
2026-04-24 | GOSD08 | SV117.01 | PQ3-Week3 | TRUE | WATER SYSTEM (B10) | Building 10 | Return loop (B10) | PW | 2026-04-25 | 2026-04-29 | 0 | 0 | 0 |  | 100 | PASSED | FALSE | WT-26-0056 | complete | pending
2026-04-24 | OSD01 | SV116.15 | PQ3-Week3 | TRUE | 10-4-012 | Building 10 | CIP SKID-1 FOR BIN WASHING-1 | PW | 2026-04-25 | 2026-04-29 | 9 | 4 | 7 |  | 100 | PASSED | FALSE | WT-26-0056 | complete | pending
2026-04-24 | OSD02 | SV116.16 | PQ3-Week3 | TRUE | 10-4-012 | Building 10 | WIP SKID-3 FOR GRANULATION POTENT | PW | 2026-04-25 | 2026-04-29 | 99 | 94 | 97 |  | 100 | PASSED | FALSE | WT-26-0056 | complete | pending
2026-04-24 | OSD03 | SV116.17 | PQ3-Week3 | TRUE | 10-4-012 | Building 10 | CIP SKID-2 FOR BIN WASHING-1 | PW | 2026-04-25 | 2026-04-29 | 28 | 8 | 18 |  | 100 | PASSED | FALSE | WT-26-0056 | complete | pending
2026-04-24 | OSD04 | SV116.18 | PQ3-Week3 | TRUE | 10-4-012 | Building 10 | WIP SKID-1 FOR GRANULATION NON POTENT | PW | 2026-04-25 | 2026-04-29 | 0 | 0 | 0 |  | 100 | PASSED | FALSE | WT-26-0056 | complete | pending
2026-04-24 | OSD05 | SV116.19 | PQ3-Week3 | TRUE | 10-4-012 | Building 10 | WIP SKID-2 FOR GRANULATION NON POTENT | PW | 2026-04-25 | 2026-04-29 | 42 | 21 | 32 |  | 100 | PASSED | FALSE | WT-26-0056 | complete | pending
2026-04-24 | OSD34 | SV116.02 | PQ3-Week3 | TRUE | 10-2-037 | Building 10 | SKID FOR BIN WASHING-2 | PW | 2026-04-25 | 2026-04-29 | 0 | 0 | 0 |  | 100 | PASSED | FALSE | WT-26-0056 | complete | pending
2026-04-24 | OSD35 | SV116.01 | PQ3-Week3 | TRUE | 10-2-021 | Building 10 | INSTRUMENT-1 | PW | 2026-04-25 | 2026-04-29 | 0 | 0 | 0 |  | 100 | PASSED | FALSE | WT-26-0056 | complete | pending
2026-04-24 | OSD36 | DV116.03 | PQ3-Week3 | TRUE | 10-2-034 | Building 10 | SAMPLE PREPARATION | PW | 2026-04-25 | 2026-04-29 |  |  | #DIV/0! |  | 100 | NA | FALSE | WT-26-0056 | complete | pending
2026-04-24 | OSD37 | DV116.06 | PQ3-Week3 | TRUE | 10-2-034 | Building 10 | SAMPLE PREPARATION | PW | 2026-04-25 | 2026-04-29 | 0 | 0 | 0 |  | 100 | PASSED | FALSE | WT-26-0056 | complete | pending
2026-04-24 | OSD38 | DV116.07 | PQ3-Week3 | TRUE | 10-2-032 | Building 10 | GLASS-WARE WASHING | PW | 2026-04-25 | 2026-04-29 | 0 | 0 | 0 |  | 100 | PASSED | FALSE | WT-26-0056 | complete | pending
2026-04-24 | OSD39 | DV116.05 | PQ3-Week3 | TRUE | 10-2-032 | Building 10 | GLASS-WARE WASHING | PW | 2026-04-25 | 2026-04-29 | 2 | 0 | 1 |  | 100 | PASSED | FALSE | WT-26-0056 | complete | pending
2026-04-24 | OSD40 | DV116.04 | PQ3-Week3 | TRUE | 10-2-037 | Building 10 | SKID FOR BIN WASHING-1 | PW | 2026-04-25 | 2026-04-29 | 0 | 0 | 0 |  | 100 | PASSED | FALSE | WT-26-0056 | complete | pending
2026-04-24 | OSD43 | DV116.26 | PQ3-Week3 | TRUE | 10-4-015 | Building 10 | WATER SYSTEM ROOM | PW | 2026-04-25 | 2026-04-29 | 0 | 0 | 0 |  | 100 | PASSED | FALSE | WT-26-0056 | complete | pending
2026-04-28 | GOCL05 | SV123.01 | PQ3-Week4 | TRUE | WATER SYSTEM (B16) | Building 16 | After Storage tank (B16) | PW | 2026-04-29 | 2026-05-06 | 0 | 0 | 0 |  | 100 | PASSED | TRUE | WT-26-0057 | complete | pending
2026-04-28 | GOCL07 | SV125.02 | PQ3-Week4 | TRUE | WATER SYSTEM (B16) | Building 16 | After UV (B16) | PW | 2026-04-29 | 2026-05-06 | 0 | 0 | 0 |  | 100 | PASSED | FALSE | WT-26-0057 | complete | pending
2026-04-28 | GOCL08 | SV127.01 | PQ3-Week4 | TRUE | WATER SYSTEM (B16) | Building 16 | Return loop (B16) | PW | 2026-04-29 | 2026-05-06 | 0 | 0 | 0 |  | 100 | PASSED | FALSE | WT-26-0057 | complete | pending
2026-04-28 | OCL11 | SV126.10 | PQ3-Week4 | TRUE | 16-3-071 | Building 16 | MFG 3 (1200L) | PW | 2026-04-29 | 2026-05-06 | 0 | 0 | 0 |  | 100 | PASSED | FALSE | WT-26-0057 | complete | pending
2026-04-28 | OCL12 | SV126.09 | PQ3-Week4 | TRUE | 16-3-071 | Building 16 | MFG 3 (5000L) | PW | 2026-04-29 | 2026-05-06 | 0 | 0 | 0 |  | 100 | PASSED | FALSE | WT-26-0057 | complete | pending
2026-04-28 | OCL15 | SV126.14 | PQ3-Week4 | TRUE | 16-3-073 | Building 16 | MFG 4 (400L) | PW | 2026-04-29 | 2026-05-06 | 0 | 0 | 0 |  | 100 | PASSED | FALSE | WT-26-0057 | complete | pending
2026-04-28 | OCL17 | SV126.15 | PQ3-Week4 | TRUE | 16-3-075 | Building 16 | MFG 5 PROCESS (2000L) | PW | 2026-04-29 | 2026-05-06 | 0 | 0 | 0 |  | 100 | PASSED | FALSE | WT-26-0057 | complete | pending
2026-04-28 | OCL21 | DV126.05 | PQ3-Week4 | TRUE | 16-3-054 | Building 16 | WASHING | PW | 2026-04-29 | 2026-05-06 | 6 | 3 | 5 |  | 100 | PASSED | FALSE | WT-26-0057 | complete | pending
2026-04-28 | OCL23 | SV126.04 | PQ3-Week4 | TRUE | 16-2-010 | Building 16 | WATER SYSTEM (PSG) | PW | 2026-04-29 | 2026-05-06 | 0 | 0 | 0 |  | 100 | PASSED | FALSE | WT-26-0057 | complete | pending
2026-04-28 | GOLD05 | SV133.01 | PQ3-Week4 | TRUE | WATER SYSTEM (B12) | Building 12 | After Storage tank (B12) | PW | 2026-04-29 | 2026-05-06 | 0 | 0 | 0 |  | 100 | PASSED | FALSE | WT-26-0058 | complete | pending
2026-04-28 | GOLD06 | SV135.02 | PQ3-Week4 | TRUE | WATER SYSTEM (B12) | Building 12 | After UV (B12) | PW | 2026-04-29 | 2026-05-06 | 0 | 0 | 0 |  | 100 | PASSED | FALSE | WT-26-0058 | complete | pending
2026-04-28 | GOLD07 | SV137.01 | PQ3-Week4 | TRUE | WATER SYSTEM (B12) | Building 12 | Return loop (B12) | PW | 2026-04-29 | 2026-05-06 | 0 | 0 | 0 |  | 100 | PASSED | FALSE | WT-26-0058 | complete | pending
2026-04-28 | OLD03 | SV136.12 | PQ3-Week4 | TRUE | 12-2-036 | Building 12 | CIP 1 | PW | 2026-04-29 | 2026-05-06 | 0 | 0 | 0 |  | 100 | PASSED | FALSE | WT-26-0058 | complete | pending
2026-04-28 | OLD04 | SV136.07 | PQ3-Week4 | TRUE | 12-2-034 | Building 12 | SYRUP PREPARATION | PW | 2026-04-29 | 2026-05-06 | 0 | 0 | 0 |  | 100 | PASSED | FALSE | WT-26-0058 | complete | pending
2026-04-28 | OLD05 | SV136.06 | PQ3-Week4 | TRUE | 12-2-034 | Building 12 | SYRUP PREPARATION | PW | 2026-04-29 | 2026-05-06 | 0 | 0 | 0 |  | 100 | PASSED | FALSE | WT-26-0058 | complete | pending
2026-04-28 | OLD08 | SV136.11 | PQ3-Week4 | TRUE | 12-2-043 | Building 12 | MFG 3 | PW | 2026-04-29 | 2026-05-06 | 0 | 0 | 0 |  | 100 | PASSED | FALSE | WT-26-0058 | complete | pending
2026-04-28 | OLD09 | SV136.13 | PQ3-Week4 | TRUE | 12-2-043 | Building 12 | MFG 3 | PW | 2026-04-29 | 2026-05-06 | 0 | 0 | 0 |  | 100 | PASSED | FALSE | WT-26-0058 | complete | pending
2026-04-28 | OLD11 | SV136.08 | PQ3-Week4 | TRUE | 12-2-043 | Building 12 | MFG 3 | PW | 2026-04-29 | 2026-05-06 | 0 | 0 | 0 |  | 100 | PASSED | FALSE | WT-26-0058 | complete | pending
2026-04-28 | OLD12 | SV136.03 | PQ3-Week4 | TRUE | 12-2-032 | Building 12 | CAMPHORATED OPIUM TINCTURE | PW | 2026-04-29 | 2026-05-06 | 0 | 0 | 0 |  | 100 | PASSED | FALSE | WT-26-0058 | complete | pending
2026-04-28 | OLD13 | SV136.05 | PQ3-Week4 | TRUE | 12-2-032 | Building 12 | CAMPHORATED OPIUM TINCTURE | PW | 2026-04-29 | 2026-05-06 | 0 | 0 | 0 |  | 100 | PASSED | FALSE | WT-26-0058 | complete | pending
2026-04-28 | OLD14 | SV136.04 | PQ3-Week4 | TRUE | 12-2-030 | Building 12 | OPIUM TINCTURE | PW | 2026-04-29 | 2026-05-06 | 0 | 0 | 0 |  | 100 | PASSED | FALSE | WT-26-0058 | complete | pending
2026-04-28 | OLD15 | DV136.02 | PQ3-Week4 | TRUE | 12-2-028 | Building 12 | ALCOHOL STORAGE | PW | 2026-04-29 | 2026-05-06 | 0 | 0 | 0 |  | 100 | PASSED | FALSE | WT-26-0058 | complete | pending
2026-04-28 | GOSD08 | SV117.01 | PQ3-Week4 | TRUE | WATER SYSTEM (B10) | Building 10 | Return loop (B10) | PW | 2026-04-29 | 2026-05-06 | 0 | 0 | 0 |  | 100 | PASSED | FALSE | WT-26-0059 | complete | pending
2026-04-28 | OCL13 | SV126.19 | PQ3-Week4 | TRUE | 16-3-087 | Building 16 | CIP 2 (EQUIPMENT REQUIREMENT) | PW | 2026-04-29 | 2026-05-06 | 0 | 0 | 0 |  | 100 | PASSED | FALSE | WT-26-0078 | complete | synced
2026-04-28 | OCL14 | DV126.11 | PQ3-Week4 | TRUE | 16-3-073 | Building 16 | MFG 4 (5000L) | PW | 2026-04-29 | 2026-05-06 | 0 | 0 | 0 |  | 100 | PASSED | FALSE | WT-26-0078 | complete | synced
2026-05-06 | GOLD02 | V50-61 (12) | PQ3-Week1 | TRUE | WATER SYSTEM (B12) | Building 12 | After Cartridge filter 5 µm (B12) | PRW | 2026-05-07 | 2026-05-12 | 277 | 265 | 271 |  | 500 | PASSED | FALSE | WT-26-0061 | complete | pending
2026-05-06 | GOLD03 | V50-11C (12) | PQ3-Week1 | TRUE | WATER SYSTEM (B12) | Building 12 | After RO (Before EDI) (B12) | RO water | 2026-05-07 | 2026-05-12 | 0 | 0 | 0 |  | 500 | PASSED | FALSE | WT-26-0061 | complete | pending
2026-05-06 | GOLD04 | V50-39 (12) | PQ3-Week1 | TRUE | WATER SYSTEM (B12) | Building 12 | After EDI (B12) | PW | 2026-05-07 | 2026-05-12 | 0 | 0 | 0 |  | 100 | PASSED | FALSE | WT-26-0061 | complete | pending
2026-05-06 | GOLD07 | SV137.01 | PQ3-Week1 | TRUE | WATER SYSTEM (B12) | Building 12 | Return loop (B12) | PW | 2026-05-07 | 2026-05-12 | 0 | 0 | 0 |  | 100 | PASSED | FALSE | WT-26-0061 | complete | pending
2026-05-06 | OLD21 | DV136.15 | PQ3-Week1 | TRUE | 12-3-078 | Building 12 | GLASSWARE WASHING 2 | PW | 2026-05-07 | 2026-05-12 | 0 | 0 | 0 |  | 100 | PASSED | FALSE | WT-26-0061 | complete | pending
2026-05-06 | OLD22 | DV136.13 | PQ3-Week1 | TRUE | 12-3-057 | Building 12 | STERILIZATION | PW | 2026-05-07 | 2026-05-12 | 0 | 0 | 0 |  | 100 | PASSED | FALSE | WT-26-0061 | complete | pending
2026-05-06 | OLD23 | SV136.18 | PQ3-Week1 | TRUE | 12-3-059 | Building 12 | AUTOCLAVE | PW | 2026-05-07 | 2026-05-12 | 0 | 0 | 0 |  | 100 | PASSED | FALSE | WT-26-0061 | complete | pending
2026-05-06 | OLD24 | DV136.11 | PQ3-Week1 | TRUE | 12-3-059 | Building 12 | AUTOCLAVE | PW | 2026-05-07 | 2026-05-12 | 0 | 0 | 0 |  | 100 | PASSED | FALSE | WT-26-0061 | complete | pending
2026-05-06 | OLD25 | DV136.12 | PQ3-Week1 | TRUE | 12-3-056 | Building 12 | MEDIA PREPARATION | PW | 2026-05-07 | 2026-05-12 | 0 | 0 | 0 |  | 100 | PASSED | FALSE | WT-26-0061 | complete | pending
2026-05-06 | OLD26 | DV136.10 | PQ3-Week1 | TRUE | 12-3-056 | Building 12 | MEDIA PREPARATION | PW | 2026-05-07 | 2026-05-12 | 0 | 0 | 0 |  | 100 | PASSED | FALSE | WT-26-0061 | complete | pending
2026-05-06 | OLD27 | DV136.14 | PQ3-Week1 | TRUE | 12-3-074 | Building 12 | DECONTAMINATION | PW | 2026-05-07 | 2026-05-12 | 0 | 0 | 0 |  | 100 | PASSED | FALSE | WT-26-0061 | complete | pending
2026-05-06 | OLD28 | DV136.18 | PQ3-Week1 | TRUE | 12-3-037 | Building 12 | GLASSWARE WASHING 1 | PW | 2026-05-07 | 2026-05-12 | 0 | 0 | 0 |  | 100 | PASSED | FALSE | WT-26-0061 | complete | pending
2026-05-06 | OLD29 | DV136.05 | PQ3-Week1 | TRUE | 12-3-037 | Building 12 | GLASSWARE WASHING 1 | PW | 2026-05-07 | 2026-05-12 | 0 | 0 | 0 |  | 100 | PASSED | FALSE | WT-26-0061 | complete | pending
2026-05-06 | OLD30 | DV136.06 | PQ3-Week1 | TRUE | 12-3-037 | Building 12 | GLASSWARE WASHING 1 | PW | 2026-05-07 | 2026-05-12 | 0 | 0 | 0 |  | 100 | PASSED | FALSE | WT-26-0061 | complete | pending
2026-05-06 | GOCL01 | VB-05 (16) | PQ3-Week1 | TRUE | WATER SYSTEM (B16) | Building 16 | After Chlorine circulation tank (B16) | PRW | 2026-05-07 | 2026-05-12 | 290 | 260 | 275 |  | 500 | PASSED | FALSE | WT-26-0062 | complete | pending
2026-05-06 | GOCL02 | V50-61 (16) | PQ3-Week1 | TRUE | WATER SYSTEM (B16) | Building 16 | After Cartridge filter 5 µm (B16) | PRW | 2026-05-07 | 2026-05-12 | 47 | 78 | 63 |  | 500 | PASSED | FALSE | WT-26-0062 | complete | pending
2026-05-06 | GOCL03 | V50-11C (16) | PQ3-Week1 | TRUE | WATER SYSTEM (B16) | Building 16 | After RO (Before EDI) (B16) | RO water | 2026-05-07 | 2026-05-12 | 0 | 0 | 0 |  | 500 | PASSED | FALSE | WT-26-0062 | complete | pending
2026-05-06 | GOCL04 | V50-39 (16) | PQ3-Week1 | TRUE | WATER SYSTEM (B16) | Building 16 | After EDI (B16) | PW | 2026-05-07 | 2026-05-12 | 0 | 0 | 0 |  | 100 | PASSED | FALSE | WT-26-0062 | complete | pending
2026-05-06 | GOCL08 | SV127.01 | PQ3-Week1 | TRUE | WATER SYSTEM (B16) | Building 16 | Return loop (B16) | PW | 2026-05-07 | 2026-05-12 | 0 | 0 | 0 |  | 100 | PASSED | FALSE | WT-26-0062 | complete | pending
2026-05-06 | OCL01 | DV126.02 | PQ3-Week1 | TRUE | 16-1-082 | Building 16 | WASHING | PW | 2026-05-07 | 2026-05-12 | 0 | 0 | 0 |  | 100 | PASSED | FALSE | WT-26-0062 | complete | pending
2026-05-06 | OCL02 | DV126.01 | PQ3-Week1 | TRUE | 16-1-082 | Building 16 | WASHING | PW | 2026-05-07 | 2026-05-12 | 0 | 0 | 0 |  | 100 | PASSED | FALSE | WT-26-0062 | complete | pending
2026-05-06 | OCL03 | SV126.02 | PQ3-Week1 | TRUE | 16-1-098 | Building 16 | CIP/SIP (EQUIPMENT REQUIREMENT – 200L) | PW | 2026-05-07 | 2026-05-12 | 0 | 0 | 0 |  | 100 | PASSED | FALSE | WT-26-0062 | complete | pending
2026-05-06 | OCL04 | DV126.03 | PQ3-Week1 | TRUE | 16-1-098 | Building 16 | CIP/SIP (SINK WASHING) | PW | 2026-05-07 | 2026-05-12 | 0 | 0 | 0 |  | 100 | PASSED | FALSE | WT-26-0062 | complete | pending
2026-05-06 | OCL05 | SV126.01 | PQ3-Week1 | TRUE | 16-1-092 | Building 16 | LINEN WASHING | PW | 2026-05-07 | 2026-05-12 | 0 | 0 | 0 |  | 100 | PASSED | FALSE | WT-26-0062 | complete | pending
2026-05-06 | OCL22 | SV126.03 | PQ3-Week1 | TRUE | 16-2-010 | Building 16 | WATER SYSTEM (WFI) | PW | 2026-05-07 | 2026-05-12 | 0 | 0 | 0 |  | 100 | PASSED | FALSE | WT-26-0062 | complete | pending
2026-05-08 | BU19-14 | SV-14 | PQ3-Week1 | TRUE | PROCESS WATER (B19) | Building 19 | AFTER RO SYSTEM NO.12 SV14 | PRW | 2026-05-09 | 2026-05-12 | 45 | 35 | 40 |  | 500 | PASSED | FALSE | WT-26-0063 | complete | pending
2026-05-08 | GOSD01 | VB-05(10) | PQ3-Week1 | TRUE | WATER SYSTEM (B10) | Building 10 | After Chlorine circulation tank (B10) | PRW | 2026-05-09 | 2026-05-12 | 58 | 39 | 49 |  | 500 | PASSED | FALSE | WT-26-0064 | complete | pending
2026-05-08 | GOSD03 | V50-61(10) | PQ3-Week1 | TRUE | WATER SYSTEM (B10) | Building 10 | After Cartridge filter 5 µm (B10) | PRW | 2026-05-09 | 2026-05-12 | 1 | 0 | 1 |  | 500 | PASSED | FALSE | WT-26-0064 | complete | pending
2026-05-08 | GOSD04 | V50-11C(10) | PQ3-Week1 | TRUE | WATER SYSTEM (B10) | Building 10 | After RO (Before EDI) (B10) | RO water | 2026-05-09 | 2026-05-12 | 0 | 0 | 0 |  | 500 | PASSED | FALSE | WT-26-0064 | complete | pending
2026-05-08 | GOSD05 | V50-39(10) | PQ3-Week1 | TRUE | WATER SYSTEM (B10) | Building 10 | After EDI (B10) | PW | 2026-05-09 | 2026-05-12 | 0 | 0 | 0 |  | 100 | PASSED | FALSE | WT-26-0064 | complete | pending
2026-05-08 | GOSD08 | SV117.01 | PQ3-Week1 | TRUE | WATER SYSTEM (B10) | Building 10 | Return loop (B10) | PW | 2026-05-09 | 2026-05-12 | 0 | 0 | 0 |  | 100 | PASSED | FALSE | WT-26-0064 | complete | pending
2026-05-08 | OSD06 | DV116.18 | PQ3-Week1 | TRUE | 10-3-111 | Building 10 | WET GRANULATION-5 | PW | 2026-05-09 | 2026-05-12 | 0 | 0 | 0 |  | 100 | PASSED | FALSE | WT-26-0064 | complete | pending
2026-05-08 | OSD07 | DV116.16 | PQ3-Week1 | TRUE | 10-3-107 | Building 10 | WET GRANULATION-2 | PW | 2026-05-09 | 2026-05-12 | 0 | 0 | 0 |  | 100 | PASSED | FALSE | WT-26-0064 | complete | pending
2026-05-08 | OSD08 | SV116.11 | PQ3-Week1 | TRUE | 10-3-107 | Building 10 | WET GRANULATION-2 | PW | 2026-05-09 | 2026-05-12 | 0 | 0 | 0 |  | 100 | PASSED | FALSE | WT-26-0064 | complete | pending
2026-05-08 | OSD09 | DV116.14 | PQ3-Week1 | TRUE | 10-3-086 | Building 10 | TOOL WASHING | PW | 2026-05-09 | 2026-05-12 | 0 | 0 | 0 |  | 100 | PASSED | FALSE | WT-26-0064 | complete | pending
2026-05-08 | OSD10 | SV116.09 | PQ3-Week1 | TRUE | 10-3-078 | Building 10 | WASHING | PW | 2026-05-09 | 2026-05-12 | 0 | 0 | 0 |  | 100 | PASSED | FALSE | WT-26-0064 | complete | pending
2026-05-08 | OSD11 | DV116.13 | PQ3-Week1 | TRUE | 10-3-078 | Building 10 | WASHING | PW | 2026-05-09 | 2026-05-12 | 0 | 0 | 0 |  | 100 | PASSED | FALSE | WT-26-0064 | complete | pending
2026-05-08 | OSD12 | DV116.12 | PQ3-Week1 | TRUE | 10-3-078 | Building 10 | WASHING | PW | 2026-05-09 | 2026-05-12 | 0 | 0 | 0 |  | 100 | PASSED | FALSE | WT-26-0064 | complete | pending
2026-05-08 | OSD27 | DV116.17 | PQ3-Week1 | TRUE | 10-3-117 | Building 10 | IPQC-2 | PW | 2026-05-09 | 2026-05-12 | 0 | 0 | 0 |  | 100 | PASSED | FALSE | WT-26-0064 | complete | pending
2026-05-08 | OSD28 | DV116.15 | PQ3-Week1 | TRUE | 10-3-104 | Building 10 | BINDER PREPARATION | PW | 2026-05-09 | 2026-05-12 | 184 | 83 | 134 |  | 100 | NOT-PASSED | FALSE | WT-26-0064 | complete | pending
2026-05-12 | GOLD05 | SV133.01 | PQ3-Week2 | TRUE | WATER SYSTEM (B12) | Building 12 | After Storage tank (B12) | PW | 2026-05-13 | 2026-05-16 | 0 | 0 | 0 |  | 100 | PASSED | FALSE | WT-26-0065 | complete | pending
2026-05-12 | GOLD06 | SV135.02 | PQ3-Week2 | TRUE | WATER SYSTEM (B12) | Building 12 | After UV (B12) | PW | 2026-05-13 | 2026-05-16 | 0 | 0 | 0 |  | 100 | PASSED | FALSE | WT-26-0065 | complete | pending
2026-05-12 | GOLD07 | SV137.01 | PQ3-Week2 | TRUE | WATER SYSTEM (B12) | Building 12 | Return loop (B12) | PW | 2026-05-13 | 2026-05-16 | 0 | 0 | 0 |  | 100 | PASSED | FALSE | WT-26-0065 | complete | pending
2026-05-12 | OLD03 | SV136.12 | PQ3-Week2 | TRUE | 12-2-036 | Building 12 | CIP 1 | PW | 2026-05-13 | 2026-05-16 | 0 | 0 | 0 |  | 100 | PASSED | FALSE | WT-26-0065 | complete | pending
2026-05-12 | OLD04 | SV136.07 | PQ3-Week2 | TRUE | 12-2-034 | Building 12 | SYRUP PREPARATION | PW | 2026-05-13 | 2026-05-16 | 0 | 0 | 0 |  | 100 | PASSED | FALSE | WT-26-0065 | complete | pending
2026-05-12 | OLD05 | SV136.06 | PQ3-Week2 | TRUE | 12-2-034 | Building 12 | SYRUP PREPARATION | PW | 2026-05-13 | 2026-05-16 | 0 | 0 | 0 |  | 100 | PASSED | FALSE | WT-26-0065 | complete | pending
2026-05-12 | OLD12 | SV136.03 | PQ3-Week2 | TRUE | 12-2-032 | Building 12 | CAMPHORATED OPIUM TINCTURE | PW | 2026-05-13 | 2026-05-16 | 0 | 0 | 0 |  | 100 | PASSED | FALSE | WT-26-0065 | complete | pending
2026-05-12 | OLD13 | SV136.05 | PQ3-Week2 | TRUE | 12-2-032 | Building 12 | CAMPHORATED OPIUM TINCTURE | PW | 2026-05-13 | 2026-05-16 | 0 | 0 | 0 |  | 100 | PASSED | FALSE | WT-26-0065 | complete | pending
2026-05-12 | OLD14 | SV136.04 | PQ3-Week2 | TRUE | 12-2-030 | Building 12 | OPIUM TINCTURE | PW | 2026-05-13 | 2026-05-16 | 0 | 0 | 0 |  | 100 | PASSED | FALSE | WT-26-0065 | complete | pending
2026-05-12 | OLD15 | DV136.02 | PQ3-Week2 | TRUE | 12-2-028 | Building 12 | ALCOHOL STORAGE | PW | 2026-05-13 | 2026-05-16 | 0 | 0 | 0 |  | 100 | PASSED | FALSE | WT-26-0065 | complete | pending
2026-05-12 | OLD31 | DV136.07 | PQ3-Week2 | TRUE | 12-3-039 | Building 12 | INSTRUMENT 7 | PW | 2026-05-13 | 2026-05-16 | 0 | 0 | 0 |  | 100 | PASSED | FALSE | WT-26-0065 | complete | pending
2026-05-12 | GOCL05 | SV123.01 | PQ3-Week2 | TRUE | WATER SYSTEM (B16) | Building 16 | After Storage tank (B16) | PW | 2026-05-13 | 2026-05-16 | 0 | 0 | 0 |  | 100 | PASSED | FALSE | WT-26-0079 | complete | synced
2026-05-12 | GOCL07 | SV125.02 | PQ3-Week2 | TRUE | WATER SYSTEM (B16) | Building 16 | After UV (B16) | PW | 2026-05-13 | 2026-05-16 | 0 | 0 | 0 |  | 100 | PASSED | FALSE | WT-26-0066 | complete | pending
2026-05-12 | GOCL08 | SV127.01 | PQ3-Week2 | TRUE | WATER SYSTEM (B16) | Building 16 | Return loop (B16) | PW | 2026-05-13 | 2026-05-16 | 0 | 0 | 0 |  | 100 | PASSED | FALSE | WT-26-0066 | complete | pending
2026-05-12 | OCL09 | DV126.10 | PQ3-Week2 | TRUE | 16-3-069 | Building 16 | MFG 2 | PW | 2026-05-13 | 2026-05-16 | 0 | 0 | 0 |  | 100 | PASSED | FALSE | WT-26-0066 | complete | pending
2026-05-12 | OCL10 | DV126.06 | PQ3-Week2 | TRUE | 16-3-069 | Building 16 | MFG 2 | PW | 2026-05-13 | 2026-05-16 | 0 | 0 | 0 |  | 100 | PASSED | FALSE | WT-26-0066 | complete | pending
2026-05-12 | OCL11 | SV126.10 | PQ3-Week2 | TRUE | 16-3-071 | Building 16 | MFG 3 (1200L) | PW | 2026-05-13 | 2026-05-16 | 0 | 0 | 0 |  | 100 | PASSED | FALSE | WT-26-0066 | complete | pending
2026-05-12 | OCL12 | SV126.09 | PQ3-Week2 | TRUE | 16-3-071 | Building 16 | MFG 3 (5000L) | PW | 2026-05-13 | 2026-05-16 | 0 | 0 | 0 |  | 100 | PASSED | FALSE | WT-26-0066 | complete | pending
2026-05-12 | OCL18 | DV126.08 | PQ3-Week2 | TRUE | 16-3-077 | Building 16 | MFG 6 | PW | 2026-05-13 | 2026-05-16 | 0 | 0 | 0 |  | 100 | PASSED | FALSE | WT-26-0066 | complete | pending
2026-05-12 | OCL19 | DV126.07 | PQ3-Week2 | TRUE | 16-3-077 | Building 16 | MFG 6 | PW | 2026-05-13 | 2026-05-16 | 0 | 0 | 0 |  | 100 | PASSED | FALSE | WT-26-0066 | complete | pending
2026-05-15 | GOSD06 | SV113.01 | PQ3-Week2 | TRUE | WATER SYSTEM (B10) | Building 10 | After Storage tank (B10) | PW | 2026-05-16 | 2026-05-19 | 0 | 0 | 0 |  | 100 | PASSED | FALSE | WT-26-0067 | complete | pending
2026-05-15 | GOSD07 | SV115.02 | PQ3-Week2 | TRUE | WATER SYSTEM (B10) | Building 10 | After UV (B10) | PW | 2026-05-16 | 2026-05-19 | 0 | 0 | 0 |  | 100 | PASSED | FALSE | WT-26-0067 | complete | pending
2026-05-15 | GOSD08 | SV117.01 | PQ3-Week2 | TRUE | WATER SYSTEM (B10) | Building 10 | Return loop (B10) | PW | 2026-05-16 | 2026-05-19 | 0 | 0 | 0 |  | 100 | PASSED | FALSE | WT-26-0067 | complete | pending
2026-05-15 | OSD22 | SV116.05 | PQ3-Week2 | TRUE | 10-3-062 | Building 10 | COATING ROOM-3 | PW | 2026-05-16 | 2026-05-19 | 0 | 0 | 0 |  | 100 | PASSED | FALSE | WT-26-0067 | complete | pending
2026-05-15 | OSD23 | SV116.04 | PQ3-Week2 | TRUE | 10-3-061 | Building 10 | COATING ROOM-2 | PW | 2026-05-16 | 2026-05-19 | 0 | 0 | 0 |  | 100 | PASSED | FALSE | WT-26-0067 | complete | pending
2026-05-15 | OSD24 | DV116.09 | PQ3-Week2 | TRUE | 10-3-060 | Building 10 | COATING SOLUTION PREP.-2 | PW | 2026-05-16 | 2026-05-19 | 0 | 0 | 0 |  | 100 | PASSED | FALSE | WT-26-0067 | complete | pending
2026-05-15 | OSD25 | DV116.08 | PQ3-Week2 | TRUE | 10-3-059 | Building 10 | COATING SOLUTION PREP.-1 | PW | 2026-05-16 | 2026-05-19 | 0 | 0 | 0 |  | 100 | PASSED | FALSE | WT-26-0067 | complete | pending
2026-05-15 | OSD26 | SV116.03 | PQ3-Week2 | TRUE | 10-3-058 | Building 10 | COATING ROOM-1 | PW | 2026-05-16 | 2026-05-19 | 0 | 0 | 0 |  | 100 | PASSED | FALSE | WT-26-0067 | complete | pending
2026-05-15 | OSD29 | SV116.08 | PQ3-Week2 | TRUE | 10-3-067 | Building 10 | COATING ROOM-6 | PW | 2026-05-16 | 2026-05-19 | 0 | 0 | 0 |  | 100 | PASSED | FALSE | WT-26-0067 | complete | pending
2026-05-15 | OSD30 | DV116.11 | PQ3-Week2 | TRUE | 10-3-066 | Building 10 | COATING SOLUTION PREP.-4 | PW | 2026-05-16 | 2026-05-19 | 0 | 0 | 0 |  | 100 | PASSED | FALSE | WT-26-0067 | complete | pending
2026-05-15 | OSD31 | DV116.10 | PQ3-Week2 | TRUE | 10-3-065 | Building 10 | COATING SOLUTION PREP.-3 | PW | 2026-05-16 | 2026-05-19 | 0 | 0 | 0 |  | 100 | PASSED | FALSE | WT-26-0067 | complete | pending
2026-05-15 | OSD32 | SV116.07 | PQ3-Week2 | TRUE | 10-3-064 | Building 10 | COATING ROOM-5 | PW | 2026-05-16 | 2026-05-19 | 0 | 0 | 0 |  | 100 | PASSED | FALSE | WT-26-0067 | complete | pending
2026-05-15 | OSD33 | SV116.06 | PQ3-Week2 | TRUE | 10-3-063 | Building 10 | COATING ROOM-4 | PW | 2026-05-16 | 2026-05-19 | 0 | 0 | 0 |  | 100 | PASSED | FALSE | WT-26-0067 | complete | pending
2026-05-15 | OSD36 | DV116.03 | PQ3-Week2 | TRUE | 10-2-034 | Building 10 | SAMPLE PREPARATION | PW | 2026-05-16 | 2026-05-19 | 0 | 0 | 0 |  | 100 | PASSED | FALSE | WT-26-0067 | complete | pending
2026-05-15 | OSD37 | DV116.06 | PQ3-Week2 | TRUE | 10-2-034 | Building 10 | SAMPLE PREPARATION | PW | 2026-05-16 | 2026-05-19 | 0 | 0 | 0 |  | 100 | PASSED | FALSE | WT-26-0067 | complete | pending
2026-05-15 | OSD38 | DV116.07 | PQ3-Week2 | TRUE | 10-2-032 | Building 10 | GLASS-WARE WASHING | PW | 2026-05-16 | 2026-05-19 | 0 | 0 | 0 |  | 100 | PASSED | FALSE | WT-26-0067 | complete | pending
2026-05-15 | OSD39 | DV116.05 | PQ3-Week2 | TRUE | 10-2-032 | Building 10 | GLASS-WARE WASHING | PW | 2026-05-16 | 2026-05-19 | 0 | 0 | 0 |  | 100 | PASSED | FALSE | WT-26-0067 | complete | pending
2026-05-15 | OSD40 | DV116.04 | PQ3-Week2 | TRUE | 10-2-037 | Building 10 | SKID FOR BIN WASHING-1 | PW | 2026-05-16 | 2026-05-19 | 0 | 0 | 0 |  | 100 | PASSED | FALSE | WT-26-0067 | complete | pending
2026-05-15 | B11 | #N/A | PQ3-Week2 | TRUE | #N/A | Building 11 | #N/A | #N/A | 2026-05-16 | 2026-05-20 | 0 | 0 | 0 |  | #N/A | NA | FALSE | WT-26-0080 | complete | synced
2026-05-19 | GOLD02 | V50-61 (12) | PQ3-Week3 | TRUE | WATER SYSTEM (B12) | Building 12 | After Cartridge filter 5 µm (B12) | PRW | 2026-05-20 | 2026-05-21 | 0 | 0 | 0 |  | 500 | PASSED | FALSE | WT-26-0081 | complete | synced
2026-05-19 | GOLD03 | V50-11C (12) | PQ3-Week3 | TRUE | WATER SYSTEM (B12) | Building 12 | After RO (Before EDI) (B12) | PRW | 2026-05-20 | 2026-05-23 | 0 | 0 | 0 |  | 500 | PASSED | FALSE | WT-26-0081 | complete | synced
2026-05-19 | GOLD04 | V50-39 (12) | PQ3-Week3 | TRUE | WATER SYSTEM (B12) | Building 12 | After EDI (B12) | RO water | 2026-05-20 | 2026-05-23 | 0 | 0 | 0 |  | 500 | PASSED | FALSE | WT-26-0081 | complete | synced
2026-05-19 | GOLD07 | SV137.01 | PQ3-Week3 | TRUE | WATER SYSTEM (B12) | Building 12 | Return loop (B12) | PW | 2026-05-20 | 2026-05-23 | 0 | 0 | 0 |  | 100 | PASSED | FALSE | WT-26-0081 | complete | synced
2026-05-19 | OLD01 | DV136.17 | PQ3-Week3 | TRUE | WATER SYSTEM (B12) | Building 12 | WASHING | PW | 2026-05-20 | 2026-05-23 | 0 | 0 | 0 |  | 100 | PASSED | FALSE | WT-26-0081 | complete | synced
2026-05-19 | OLD02 | SV136.16 | PQ3-Week3 | TRUE | 12-2-065 | Building 12 | CIP 2 | PW | 2026-05-20 | 2026-05-23 | 0 | 0 | 0 |  | 100 | PASSED | FALSE | WT-26-0081 | complete | synced
2026-05-19 | OLD10 | SV136.15 | PQ3-Week3 | TRUE | 12-2-057 | Building 12 | CIP 3 | PW | 2026-05-20 | 2026-05-23 | 0 | 0 | 0 |  | 100 | PASSED | FALSE | WT-26-0081 | complete | synced
2026-05-19 | OLD17 | DV136.03 | PQ3-Week3 | TRUE | 12-2-055 | Building 12 | IPQC | PW | 2026-05-20 | 2026-05-23 | 0 | 0 | 0 |  | 100 | PASSED | FALSE | WT-26-0081 | complete | synced
2026-05-19 | OLD19 | DV136.01 | PQ3-Week3 | TRUE | 12-2-053 | Building 12 | SUGAR TRANSFERRING | PW | 2026-05-20 | 2026-05-23 | 0 | 0 | 0 |  | 100 | PASSED | FALSE | WT-26-0081 | complete | synced
2026-05-19 | OLD20 | DV136.16 | PQ3-Week3 | TRUE | 12-1-035 | Building 12 | WASHING | PW | 2026-05-20 | 2026-05-23 | 0 | 0 | 0 |  | 100 | PASSED | FALSE | WT-26-0081 | complete | synced
2026-05-19 | OLD34 | DV136.04 | PQ3-Week3 | TRUE | 12-1-064 | Building 12 | WATER SYSTEM ROOM | PW | 2026-05-20 | 2026-05-23 | 0 | 0 | 0 |  | 100 | PASSED | FALSE | WT-26-0081 | complete | synced
2026-05-19 | GOCL01 | VB-05 (16) | PQ3-Week3 | TRUE | WATER SYSTEM (B16) | Building 16 | After Chlorine circulation tank (B16) | PRW | 2026-05-20 | 2026-05-23 | 0 | 0 | 0 |  | 500 | PASSED | FALSE | WT-26-0069 | complete | pending
2026-05-19 | GOCL02 | V50-61 (16) | PQ3-Week3 | TRUE | WATER SYSTEM (B16) | Building 16 | After Cartridge filter 5 µm (B16) | PRW | 2026-05-20 | 2026-05-23 | 0 | 0 | 0 |  | 500 | PASSED | FALSE | WT-26-0069 | complete | pending
2026-05-19 | GOCL03 | V50-11C (16) | PQ3-Week3 | TRUE | WATER SYSTEM (B16) | Building 16 | After RO (Before EDI) (B16) | RO water | 2026-05-20 | 2026-05-23 | 0 | 0 | 0 |  | 500 | PASSED | FALSE | WT-26-0069 | complete | pending
2026-05-19 | GOCL04 | V50-39 (16) | PQ3-Week3 | TRUE | WATER SYSTEM (B16) | Building 16 | After EDI (B16) | PW | 2026-05-20 | 2026-05-23 | 0 | 0 | 0 |  | 100 | PASSED | FALSE | WT-26-0069 | complete | pending
2026-05-19 | GOCL08 | SV127.01 | PQ3-Week3 | TRUE | WATER SYSTEM (B16) | Building 16 | Return loop (B16) | PW | 2026-05-20 | 2026-05-23 | 0 | 0 | 0 |  | 100 | PASSED | FALSE | WT-26-0069 | complete | pending
2026-05-19 | OCL06 | SV126.06 | PQ3-Week3 | TRUE | 16-3-067 | Building 16 | MFG 1 | PW | 2026-05-20 | 2026-05-23 | 0 | 0 | 0 |  | 100 | PASSED | FALSE | WT-26-0069 | complete | pending
2026-05-19 | OCL07 | SV126.21 | PQ3-Week3 | TRUE | 16-3-090 | Building 16 | CIP 1 (EQUIPMENT REQUIREMENT) | PW | 2026-05-20 | 2026-05-23 | 0 | 0 | 0 |  | 100 | PASSED | FALSE | WT-26-0069 | complete | pending
2026-05-19 | OCL08 | DV126.09 | PQ3-Week3 | TRUE | 16-3-090 | Building 16 | CIP 1 (ZINK WASHING) | PW | 2026-05-20 | 2026-05-23 | 0 | 0 | 0 |  | 100 | PASSED | FALSE | WT-26-0069 | complete | pending
2026-05-19 | OCL16 | SV126.18 | PQ3-Week3 | TRUE | 16-3-085 | Building 16 | CIP 3 (EQUIPMENT REQUIREMENT) | PW | 2026-05-20 | 2026-05-23 | 0 | 0 | 0 |  | 100 | PASSED | FALSE | WT-26-0069 | complete | pending
2026-05-19 | OCL20 | SV126.05 | PQ3-Week3 | TRUE | 16-3-049 | Building 16 | LINEN WASHING | PW | 2026-05-20 | 2026-05-23 | 0 | 0 | 0 |  | 100 | PASSED | FALSE | WT-26-0069 | complete | pending
2026-05-19 | OCL23 | SV126.04 | PQ3-Week3 | TRUE | 16-2-010 | Building 16 | WATER SYSTEM (PSG) | PW | 2026-05-20 | 2026-05-23 | 0 | 0 | 0 |  | 100 | PASSED | FALSE | WT-26-0069 | complete | pending
2026-05-19 | OSD28 | DV116.15 | Speacial | TRUE | 10-3-104 | Building 10 | BINDER PREPARATION | PW | 2026-05-20 | 2026-05-23 | 17 | 7 | 12 | เก็บเพิ่มจาก oos | 100 | PASSED | FALSE | WT-26-0070 | complete | pending
2026-05-22 | GOSD01 | VB-05(10) | PQ3-Week3 | TRUE | WATER SYSTEM (B10) | Building 10 | After Chlorine circulation tank (B10) | PRW | 2026-05-23 | 2026-05-31 | 0 | 0 | 0 |  | 500 | PASSED |  | WT-26-0071 | complete | pending
2026-05-22 | GOSD03 | V50-61(10) | PQ3-Week3 | TRUE | WATER SYSTEM (B10) | Building 10 | After Cartridge filter 5 µm (B10) | PRW | 2026-05-23 | 2026-05-31 | 0 | 0 | 0 |  | 500 | PASSED |  | WT-26-0071 | complete | pending
2026-05-22 | GOSD04 | V50-11C(10) | PQ3-Week3 | TRUE | WATER SYSTEM (B10) | Building 10 | After RO (Before EDI) (B10) | RO water | 2026-05-23 | 2026-05-31 | 0 | 0 | 0 |  | 500 | PASSED |  | WT-26-0071 | complete | pending
2026-05-22 | GOSD05 | V50-39(10) | PQ3-Week3 | TRUE | WATER SYSTEM (B10) | Building 10 | After EDI (B10) | PW | 2026-05-23 | 2026-05-31 | 0 | 0 | 0 |  | 100 | PASSED |  | WT-26-0071 | complete | pending
2026-05-22 | GOSD06 | SV113.01 | PQ3-Week3 | TRUE | WATER SYSTEM (B10) | Building 10 | After Storage tank (B10) | PW | 2026-05-23 | 2026-05-31 | 0 | 0 | 0 |  | 100 | PASSED |  | WT-26-0071 | complete | pending
2026-05-22 | GOSD07 | SV115.02 | PQ3-Week3 | TRUE | WATER SYSTEM (B10) | Building 10 | After UV (B10) | PW | 2026-05-23 | 2026-05-31 | 0 | 0 | 0 |  | 100 | PASSED |  | WT-26-0071 | complete | pending
2026-05-22 | GOSD08 | SV117.01 | PQ3-Week3 | TRUE | WATER SYSTEM (B10) | Building 10 | Return loop (B10) | PW | 2026-05-23 | 2026-05-31 | 0 | 0 | 0 |  | 100 | PASSED |  | WT-26-0071 | complete | pending
2026-05-22 | OSD13 | DV116.25 | PQ3-Week3 | TRUE | 10-3-171 | Building 10 | TOOL WASHING-P | PW | 2026-05-23 | 2026-05-31 | 0 | 0 | 0 |  | 100 | PASSED |  | WT-26-0071 | complete | pending
2026-05-22 | OSD14 | DV116.24 | PQ3-Week3 | TRUE | 10-3-163 | Building 10 | WET GRANULATION 1-P | PW | 2026-05-23 | 2026-05-31 | 0 | 0 | 0 |  | 100 | PASSED |  | WT-26-0071 | complete | pending
2026-05-22 | OSD15 | DV116.23 | PQ3-Week3 | TRUE | 10-3-159 | Building 10 | BINDER PREPARATION-P | PW | 2026-05-23 | 2026-05-31 | 0 | 0 | 0 |  | 100 | PASSED |  | WT-26-0071 | complete | pending
2026-05-22 | OSD16 | DV116.21 | PQ3-Week3 | TRUE | 10-3-152 | Building 10 | WASHING-P | PW | 2026-05-23 | 2026-05-31 | 0 | 0 | 0 |  | 100 | PASSED |  | WT-26-0071 | complete | pending
2026-05-22 | OSD17 | DV116.22 | PQ3-Week3 | TRUE | 10-3-152 | Building 10 | WASHING-P | PW | 2026-05-23 | 2026-05-31 | 0 | 0 | 0 |  | 100 | PASSED |  | WT-26-0071 | complete | pending
2026-05-22 | OSD18 | SV116.13 | PQ3-Week3 | TRUE | 10-3-152 | Building 10 | WASHING-P | PW | 2026-05-23 | 2026-05-31 | 0 | 0 | 0 |  | 100 | PASSED |  | WT-26-0071 | complete | pending
2026-05-22 | OSD19 | DV116.20 | PQ3-Week3 | TRUE | 10-3-149 | Building 10 | IPQC-1-P | PW | 2026-05-23 | 2026-05-31 | 0 | 0 | 0 |  | 100 | PASSED |  | WT-26-0071 | complete | pending
2026-05-22 | OSD20 | DV116.19 | PQ3-Week3 | TRUE | 10-3-143 | Building 10 | COATING SOLUTION PREP.-P | PW | 2026-05-23 | 2026-05-31 | 0 | 0 | 0 |  | 100 | PASSED |  | WT-26-0071 | complete | pending
2026-05-22 | OSD21 | SV116.12 | PQ3-Week3 | TRUE | 10-3-144 | Building 10 | COATING-P | PW | 2026-05-23 | 2026-05-31 | 0 | 0 | 0 |  | 100 | PASSED |  | WT-26-0071 | complete | pending
2026-05-22 | OSD41 | DV116.02 | PQ3-Week3 | TRUE | 10-1-115 | Building 10 | WASHING | PW | 2026-05-23 | 2026-05-31 | 0 | 0 | 0 |  | 100 | PASSED |  | WT-26-0071 | complete | pending
2026-05-22 | OSD42 | DV116.01 | PQ3-Week3 | TRUE | 10-1-057 | Building 10 | WASHING-P | PW | 2026-05-23 | 2026-05-31 | 0 | 0 | 0 |  | 100 | PASSED |  | WT-26-0071 | complete | pending
2026-05-22 | BU19-14 | SV-14 | PQ3-Week3 | TRUE | PROCESS WATER (B19) | Building 19 | AFTER RO SYSTEM NO.12 SV14 | PRW | 2026-05-23 | 2026-05-31 | 0 | 0 | 0 |  | 500 | PASSED |  | WT-26-0072 | complete | pending
2026-05-26 | GOLD05 | SV133.01 | PQ3-Week4 | FALSE | WATER SYSTEM (B12) | Building 12 | After Storage tank (B12) | PW | 2026-05-26 | 2026-05-29 | 0 | 0 | 0 |  | 100 | PASSED | FALSE |  | pending
2026-05-26 | GOLD06 | SV135.02 | PQ3-Week4 | FALSE | WATER SYSTEM (B12) | Building 12 | After UV (B12) | PW | 2026-05-26 | 2026-05-29 | 0 | 0 | 0 |  | 100 | PASSED | FALSE |  | pending
2026-05-26 | GOLD07 | SV137.01 | PQ3-Week4 | FALSE | WATER SYSTEM (B12) | Building 12 | Return loop (B12) | PW | 2026-05-26 | 2026-05-29 | 0 | 0 | 0 |  | 100 | PASSED | FALSE |  | pending
2026-05-26 | OLD06 | SV136.09 | PQ3-Week4 | FALSE | 12-2-039 | Building 12 | MFG 1 | PW | 2026-05-26 | 2026-05-29 | 0 | 0 | 0 |  | 100 | PASSED | FALSE |  | pending
2026-05-26 | OLD07 | SV136.10 | PQ3-Week4 | FALSE | 12-2-041 | Building 12 | MFG 2 | PW | 2026-05-26 | 2026-05-29 | 0 | 0 | 0 |  | 100 | PASSED | FALSE |  | pending
2026-05-26 | OLD08 | SV136.11 | PQ3-Week4 | FALSE | 12-2-043 | Building 12 | MFG 3 | PW | 2026-05-26 | 2026-05-29 | 0 | 0 | 0 |  | 100 | PASSED | FALSE |  | pending
2026-05-26 | OLD09 | SV136.13 | PQ3-Week4 | FALSE | 12-2-043 | Building 12 | MFG 3 | PW | 2026-05-26 | 2026-05-29 | 0 | 0 | 0 |  | 100 | PASSED | FALSE |  | pending
2026-05-26 | OLD11 | SV136.08 | PQ3-Week4 | FALSE | 12-2-043 | Building 12 | MFG 3 | PW | 2026-05-26 | 2026-05-29 | 0 | 0 | 0 |  | 100 | PASSED | FALSE |  | pending
2026-05-26 | OLD16 | SV136.14 | PQ3-Week4 | FALSE | 12-2-045 | Building 12 | MFG 4 | PW | 2026-05-26 | 2026-05-29 | 0 | 0 | 0 |  | 100 | PASSED | FALSE |  | pending
2026-05-26 | OLD18 | SV136.02 | PQ3-Week4 | FALSE | 12-2-024 | Building 12 | LIQUORICE EXTRACT | PW | 2026-05-26 | 2026-05-29 | 0 | 0 | 0 |  | 100 | PASSED | FALSE |  | pending
2026-05-26 | OLD32 | DV136.08 | PQ3-Week4 | FALSE | 12-3-042 | Building 12 | SAMPLE PREPARATION | PW | 2026-05-26 | 2026-05-29 | 0 | 0 | 0 |  | 100 | PASSED | FALSE |  | pending
2026-05-26 | OLD33 | DV136.09 | PQ3-Week4 | FALSE | 12-3-042 | Building 12 | SAMPLE PREPARATION | PW | 2026-05-26 | 2026-05-29 | 0 | 0 | 0 |  | 100 | PASSED | FALSE |  | pending
2026-05-26 | GOCL05 | SV123.01 | PQ3-Week4 | FALSE | WATER SYSTEM (B16) | Building 16 | After Storage tank (B16) | PW | 2026-05-26 | 2026-05-29 | 0 | 0 | 0 |  | 100 | PASSED | FALSE |  | pending
2026-05-26 | GOCL07 | SV125.02 | PQ3-Week4 | FALSE | WATER SYSTEM (B16) | Building 16 | After UV (B16) | PW | 2026-05-26 | 2026-05-29 | 0 | 0 | 0 |  | 100 | PASSED | FALSE |  | pending
2026-05-26 | GOCL08 | SV127.01 | PQ3-Week4 | FALSE | WATER SYSTEM (B16) | Building 16 | Return loop (B16) | PW | 2026-05-26 | 2026-05-29 | 0 | 0 | 0 |  | 100 | PASSED | FALSE |  | pending
2026-05-26 | OCL13 | SV126.19 | PQ3-Week4 | FALSE | 16-3-087 | Building 16 | CIP 2 (EQUIPMENT REQUIREMENT) | PW | 2026-05-26 | 2026-05-29 | 0 | 0 | 0 |  | 100 | PASSED | FALSE |  | pending
2026-05-26 | OCL14 | DV126.11 | PQ3-Week4 | FALSE | 16-3-073 | Building 16 | MFG 4 (5000L) | PW | 2026-05-26 | 2026-05-29 | 0 | 0 | 0 |  | 100 | PASSED | FALSE |  | pending
2026-05-26 | OCL15 | SV126.14 | PQ3-Week4 | FALSE | 16-3-073 | Building 16 | MFG 4 (400L) | PW | 2026-05-26 | 2026-05-29 | 0 | 0 | 0 |  | 100 | PASSED | FALSE |  | pending
2026-05-26 | OCL17 | SV126.15 | PQ3-Week4 | FALSE | 16-3-075 | Building 16 | MFG 5 PROCESS (2000L) | PW | 2026-05-26 | 2026-05-29 | 0 | 0 | 0 |  | 100 | PASSED | FALSE |  | pending
2026-05-26 | OCL21 | DV126.05 | PQ3-Week4 | FALSE | 16-3-054 | Building 16 | WASHING | PW | 2026-05-26 | 2026-05-29 | 5 | 33 | 19 |  | 100 | PASSED | FALSE |  | pending
2026-05-26 | OCL23 | SV126.04 | PQ3-Week4 | FALSE | 16-2-010 | Building 16 | WATER SYSTEM (PSG) | PW | 2026-05-26 | 2026-05-29 | 0 | 0 | 0 |  | 100 | PASSED | FALSE |  | pending
2026-05-29 | GOSD08 | SV117.01 | PQ3-Week4 | FALSE | WATER SYSTEM (B10) | Building 10 | Return loop (B10) | PW | 2026-05-30 |  | 0 | 0 | 0 |  | 100 | PASSED | FALSE |  | pending
2026-05-29 | OSD01 | SV116.15 | PQ3-Week4 | FALSE | 10-4-012 | Building 10 | CIP SKID-1 FOR BIN WASHING-1 | PW | 2026-05-30 |  | 0 | 0 | 0 |  | 100 | PASSED | FALSE |  | pending
2026-05-29 | OSD02 | SV116.16 | PQ3-Week4 | FALSE | 10-4-012 | Building 10 | WIP SKID-3 FOR GRANULATION POTENT | PW | 2026-05-30 |  | 0 | 0 | 0 |  | 100 | PASSED | FALSE |  | pending
2026-05-29 | OSD03 | SV116.17 | PQ3-Week4 | FALSE | 10-4-012 | Building 10 | CIP SKID-2 FOR BIN WASHING-1 | PW | 2026-05-30 |  | 0 | 0 | 0 |  | 100 | PASSED | FALSE |  | pending
2026-05-29 | OSD04 | SV116.18 | PQ3-Week4 | FALSE | 10-4-012 | Building 10 | WIP SKID-1 FOR GRANULATION NON POTENT | PW | 2026-05-30 |  | 0 | 0 | 0 |  | 100 | PASSED | FALSE |  | pending
2026-05-29 | OSD05 | SV116.19 | PQ3-Week4 | FALSE | 10-4-012 | Building 10 | WIP SKID-2 FOR GRANULATION NON POTENT | PW | 2026-05-30 |  | 8 | 19 | 14 |  | 100 | PASSED | FALSE |  | pending
2026-05-29 | OSD34 | SV116.02 | PQ3-Week4 | FALSE | 10-2-037 | Building 10 | SKID FOR BIN WASHING-2 | PW | 2026-05-30 |  | 0 | 0 | 0 |  | 100 | PASSED | FALSE |  | pending
2026-05-29 | OSD35 | SV116.01 | PQ3-Week4 | FALSE | 10-2-021 | Building 10 | INSTRUMENT-1 | PW | 2026-05-30 |  | 0 | 0 | 0 |  | 100 | PASSED | FALSE |  | pending
2026-05-29 | OSD43 | DV116.26 | PQ3-Week4 | FALSE | 10-4-015 | Building 10 | WATER SYSTEM ROOM | PW | 2026-05-30 |  | 0 | 0 | 0 |  | 100 | PASSED | FALSE |  | pending
2026-06-02 | GOCL01 | VB-05 (16) | PQ3-Week1 | FALSE | WATER SYSTEM (B16) | Building 16 | After Chlorine circulation tank (B16) | PRW | 2026-06-03 | 2026-06-06 | 4 | 1 | 3 |  | 500 | PASSED | FALSE |  | pending
2026-06-02 | GOCL02 | V50-61 (16) | PQ3-Week1 | FALSE | WATER SYSTEM (B16) | Building 16 | After Cartridge filter 5 µm (B16) | PRW | 2026-06-03 | 2026-06-06 | 1 | 0 | 1 |  | 500 | PASSED | FALSE |  | pending
2026-06-02 | GOCL03 | V50-11C (16) | PQ3-Week1 | FALSE | WATER SYSTEM (B16) | Building 16 | After RO (Before EDI) (B16) | RO water | 2026-06-03 | 2026-06-06 | 0 | 0 | 0 |  | 500 | PASSED | FALSE |  | pending
2026-06-02 | GOCL04 | V50-39 (16) | PQ3-Week1 | FALSE | WATER SYSTEM (B16) | Building 16 | After EDI (B16) | PW | 2026-06-03 | 2026-06-06 | 0 | 0 | 0 |  | 100 | PASSED | FALSE |  | pending
2026-06-02 | GOCL08 | SV127.01 | PQ3-Week1 | FALSE | WATER SYSTEM (B16) | Building 16 | Return loop (B16) | PW | 2026-06-03 | 2026-06-06 | 0 | 0 | 0 |  | 100 | PASSED | FALSE |  | pending
2026-06-02 | OCL01 | DV126.02 | PQ3-Week1 | FALSE | 16-1-082 | Building 16 | WASHING | PW | 2026-06-03 | 2026-06-06 | 0 | 0 | 0 |  | 100 | PASSED | FALSE |  | pending
2026-06-02 | OCL02 | DV126.01 | PQ3-Week1 | FALSE | 16-1-082 | Building 16 | WASHING | PW | 2026-06-03 | 2026-06-06 | 0 | 0 | 0 |  | 100 | PASSED | FALSE |  | pending
2026-06-02 | OCL03 | SV126.02 | PQ3-Week1 | FALSE | 16-1-098 | Building 16 | CIP/SIP (EQUIPMENT REQUIREMENT – 200L) | PW | 2026-06-03 | 2026-06-06 | 0 | 0 | 0 |  | 100 | PASSED | FALSE |  | pending
2026-06-02 | OCL04 | DV126.03 | PQ3-Week1 | FALSE | 16-1-098 | Building 16 | CIP/SIP (SINK WASHING) | PW | 2026-06-03 | 2026-06-06 | 0 | 0 | 0 |  | 100 | PASSED | FALSE |  | pending
2026-06-02 | OCL05 | SV126.01 | PQ3-Week1 | FALSE | 16-1-092 | Building 16 | LINEN WASHING | PW | 2026-06-03 | 2026-06-06 | 0 | 0 | 0 |  | 100 | PASSED | FALSE |  | pending
2026-06-02 | OCL22 | SV126.03 | PQ3-Week1 | FALSE | 16-2-010 | Building 16 | WATER SYSTEM (WFI) | PW | 2026-06-03 | 2026-06-06 | 0 | 0 | 0 |  | 100 | PASSED | FALSE |  | pending
2026-06-02 | GOLD01 | VB-05 (12) | PQ3-Week1 | FALSE | WATER SYSTEM (B12) | Building 12 | After Chlorine circulation tank | PRW | 2026-06-03 | 2026-06-06 |  |  | #DIV/0! |  | 500 | NA | FALSE |  | pending
2026-06-02 | GOLD02 | V50-61 (12) | PQ3-Week1 | FALSE | WATER SYSTEM (B12) | Building 12 | After Cartridge filter 5 µm (B12) | PRW | 2026-06-03 | 2026-06-06 | 163 | 144 | 154 |  | 500 | PASSED | FALSE |  | pending
2026-06-02 | GOLD03 | V50-11C (12) | PQ3-Week1 | FALSE | WATER SYSTEM (B12) | Building 12 | After RO (Before EDI) (B12) | RO water | 2026-06-03 | 2026-06-06 | 0 | 0 | 0 |  | 500 | PASSED | FALSE |  | pending
2026-06-02 | GOLD04 | V50-39 (12) | PQ3-Week1 | FALSE | WATER SYSTEM (B12) | Building 12 | After EDI (B12) | PW | 2026-06-03 | 2026-06-06 | 0 | 0 | 0 |  | 100 | PASSED | FALSE |  | pending
2026-06-02 | GOLD07 | SV137.01 | PQ3-Week1 | FALSE | WATER SYSTEM (B12) | Building 12 | Return loop (B12) | PW | 2026-06-03 | 2026-06-06 | 0 | 0 | 0 |  | 100 | PASSED | FALSE |  | pending
2026-06-02 | OLD21 | DV136.15 | PQ3-Week1 | FALSE | 12-3-078 | Building 12 | GLASSWARE WASHING 2 | PW | 2026-06-03 | 2026-06-06 | 0 | 0 | 0 |  | 100 | PASSED | FALSE |  | pending
2026-06-02 | OLD22 | DV136.13 | PQ3-Week1 | FALSE | 12-3-057 | Building 12 | STERILIZATION | PW | 2026-06-03 | 2026-06-06 | 0 | 0 | 0 |  | 100 | PASSED | FALSE |  | pending
2026-06-02 | OLD23 | SV136.18 | PQ3-Week1 | FALSE | 12-3-059 | Building 12 | AUTOCLAVE | PW | 2026-06-03 | 2026-06-06 | 0 | 0 | 0 |  | 100 | PASSED | FALSE |  | pending
2026-06-02 | OLD24 | DV136.11 | PQ3-Week1 | FALSE | 12-3-059 | Building 12 | AUTOCLAVE | PW | 2026-06-03 | 2026-06-06 | 0 | 0 | 0 |  | 100 | PASSED | FALSE |  | pending
2026-06-02 | OLD25 | DV136.12 | PQ3-Week1 | FALSE | 12-3-056 | Building 12 | MEDIA PREPARATION | PW | 2026-06-03 | 2026-06-06 | 0 | 0 | 0 |  | 100 | PASSED | FALSE |  | pending
2026-06-02 | OLD26 | DV136.10 | PQ3-Week1 | FALSE | 12-3-056 | Building 12 | MEDIA PREPARATION | PW | 2026-06-03 | 2026-06-06 | 0 | 0 | 0 |  | 100 | PASSED | FALSE |  | pending
2026-06-02 | OLD27 | DV136.14 | PQ3-Week1 | FALSE | 12-3-074 | Building 12 | DECONTAMINATION | PW | 2026-06-03 | 2026-06-06 | 0 | 0 | 0 |  | 100 | PASSED | FALSE |  | pending
2026-06-02 | OLD28 | DV136.18 | PQ3-Week1 | FALSE | 12-3-037 | Building 12 | GLASSWARE WASHING 1 | PW | 2026-06-03 | 2026-06-06 | 0 | 0 | 0 |  | 100 | PASSED | FALSE |  | pending
2026-06-02 | OLD29 | DV136.05 | PQ3-Week1 | FALSE | 12-3-037 | Building 12 | GLASSWARE WASHING 1 | PW | 2026-06-03 | 2026-06-06 | 0 | 0 | 0 |  | 100 | PASSED | FALSE |  | pending
2026-06-02 | OLD30 | DV136.06 | PQ3-Week1 | FALSE | 12-3-037 | Building 12 | GLASSWARE WASHING 1 | PW | 2026-06-03 | 2026-06-06 | 0 | 0 | 0 |  | 100 | PASSED | FALSE |  | pending
2026-06-05 | GOSD01 | VB-05(10) | PQ3-Week1 | FALSE | WATER SYSTEM (B10) | Building 10 | After Chlorine circulation tank (B10) | PRW | 2026-06-05 | 2026-06-08 | 10 | 21 | 16 |  | 500 | PASSED | FALSE |  | pending
2026-06-05 | GOSD03 | V50-61(10) | PQ3-Week1 | FALSE | WATER SYSTEM (B10) | Building 10 | After Cartridge filter 5 µm (B10) | PRW | 2026-06-05 | 2026-06-08 | 4 | 5 | 5 |  | 500 | PASSED | FALSE |  | pending
2026-06-05 | GOSD04 | V50-11C(10) | PQ3-Week1 | FALSE | WATER SYSTEM (B10) | Building 10 | After RO (Before EDI) (B10) | RO water | 2026-06-05 | 2026-06-08 | 0 | 0 | 0 |  | 500 | PASSED | FALSE |  | pending
2026-06-05 | GOSD05 | V50-39(10) | PQ3-Week1 | FALSE | WATER SYSTEM (B10) | Building 10 | After EDI (B10) | PW | 2026-06-05 | 2026-06-08 | 0 | 0 | 0 |  | 100 | PASSED | FALSE |  | pending
2026-06-05 | GOSD08 | SV117.01 | PQ3-Week1 | FALSE | WATER SYSTEM (B10) | Building 10 | Return loop (B10) | PW | 2026-06-05 | 2026-06-08 | 0 | 0 | 0 |  | 100 | PASSED | FALSE |  | pending
2026-06-05 | OSD06 | DV116.18 | PQ3-Week1 | FALSE | 10-3-111 | Building 10 | WET GRANULATION-5 | PW | 2026-06-05 | 2026-06-08 | 0 | 0 | 0 |  | 100 | PASSED | FALSE |  | pending
2026-06-05 | OSD07 | DV116.16 | PQ3-Week1 | FALSE | 10-3-107 | Building 10 | WET GRANULATION-2 | PW | 2026-06-05 | 2026-06-08 | 0 | 0 | 0 |  | 100 | PASSED | FALSE |  | pending
2026-06-05 | OSD08 | SV116.11 | PQ3-Week1 | FALSE | 10-3-107 | Building 10 | WET GRANULATION-2 | PW | 2026-06-05 | 2026-06-08 | 0 | 0 | 0 |  | 100 | PASSED | FALSE |  | pending
2026-06-05 | OSD09 | DV116.14 | PQ3-Week1 | FALSE | 10-3-086 | Building 10 | TOOL WASHING | PW | 2026-06-05 | 2026-06-08 | 0 | 0 | 0 |  | 100 | PASSED | FALSE |  | pending
2026-06-05 | OSD10 | SV116.09 | PQ3-Week1 | FALSE | 10-3-078 | Building 10 | WASHING | PW | 2026-06-05 | 2026-06-08 | 0 | 0 | 0 |  | 100 | PASSED | FALSE |  | pending
2026-06-05 | OSD11 | DV116.13 | PQ3-Week1 | FALSE | 10-3-078 | Building 10 | WASHING | PW | 2026-06-05 | 2026-06-08 | 0 | 0 | 0 |  | 100 | PASSED | FALSE |  | pending
2026-06-05 | OSD12 | DV116.12 | PQ3-Week1 | FALSE | 10-3-078 | Building 10 | WASHING | PW | 2026-06-05 | 2026-06-08 | 0 | 0 | 0 |  | 100 | PASSED | FALSE |  | pending
2026-06-05 | OSD27 | DV116.17 | PQ3-Week1 | FALSE | 10-3-117 | Building 10 | IPQC-2 | PW | 2026-06-05 | 2026-06-08 | 0 | 0 | 0 |  | 100 | PASSED | FALSE |  | pending
2026-06-05 | OSD28 | DV116.15 | PQ3-Week1 | FALSE | 10-3-104 | Building 10 | BINDER PREPARATION | PW | 2026-06-05 | 2026-06-08 | 0 | 0 | 0 |  | 100 | PASSED | FALSE |  | pending
2026-06-05 | BU19-14 | SV-14 | PQ3-Week1 | FALSE | PROCESS WATER (B19) | Building 19 | AFTER RO SYSTEM NO.12 SV14 | PRW | 2026-06-05 | 2026-06-08 | 130 | 138 | 134 |  | 500 | PASSED | FALSE |  | pending
2026-06-09 | GOCL05 | SV123.01 | PQ3-Week2 | FALSE | WATER SYSTEM (B16) | Building 16 | After Storage tank (B16) | PW | 2026-06-10 |  |  |  | #DIV/0! |  | 100 | NA | FALSE |  | pending
2026-06-09 | GOCL07 | SV125.02 | PQ3-Week2 | FALSE | WATER SYSTEM (B16) | Building 16 | After UV (B16) | PW | 2026-06-10 |  |  |  | #DIV/0! |  | 100 | NA | FALSE |  | pending
2026-06-09 | GOCL08 | SV127.01 | PQ3-Week2 | FALSE | WATER SYSTEM (B16) | Building 16 | Return loop (B16) | PW | 2026-06-10 |  |  |  | #DIV/0! |  | 100 | NA | FALSE |  | pending
2026-06-09 | OCL13 | SV126.19 | PQ3-Week2 | FALSE | 16-3-087 | Building 16 | CIP 2 (EQUIPMENT REQUIREMENT) | PW | 2026-06-10 |  |  |  | #DIV/0! |  | 100 | NA | FALSE |  | pending
2026-06-09 | OCL14 | DV126.11 | PQ3-Week2 | FALSE | 16-3-073 | Building 16 | MFG 4 (5000L) | PW | 2026-06-10 |  |  |  | #DIV/0! |  | 100 | NA | FALSE |  | pending
2026-06-09 | OCL15 | SV126.14 | PQ3-Week2 | FALSE | 16-3-073 | Building 16 | MFG 4 (400L) | PW | 2026-06-10 |  |  |  | #DIV/0! |  | 100 | NA | FALSE |  | pending
2026-06-09 | OCL17 | SV126.15 | PQ3-Week2 | FALSE | 16-3-075 | Building 16 | MFG 5 PROCESS (2000L) | PW | 2026-06-10 |  |  |  | #DIV/0! |  | 100 | NA | FALSE |  | pending
2026-06-09 | OCL21 | DV126.05 | PQ3-Week2 | FALSE | 16-3-054 | Building 16 | WASHING | PW | 2026-06-10 |  |  |  | #DIV/0! |  | 100 | NA | FALSE |  | pending
2026-06-09 | OCL23 | SV126.04 | PQ3-Week2 | FALSE | 16-2-010 | Building 16 | WATER SYSTEM (PSG) | PW | 2026-06-10 |  |  |  | #DIV/0! |  | 100 | NA | FALSE |  | pending
2026-06-09 | GOLD05 | SV133.01 | PQ3-Week2 | FALSE | WATER SYSTEM (B12) | Building 12 | After Storage tank (B12) | PW | 2026-06-10 |  |  |  | #DIV/0! |  | 100 | NA | FALSE |  | pending
2026-06-09 | GOLD06 | SV135.02 | PQ3-Week2 | FALSE | WATER SYSTEM (B12) | Building 12 | After UV (B12) | PW | 2026-06-10 |  |  |  | #DIV/0! |  | 100 | NA | FALSE |  | pending
2026-06-09 | GOLD07 | SV137.01 | PQ3-Week2 | FALSE | WATER SYSTEM (B12) | Building 12 | Return loop (B12) | PW | 2026-06-10 |  |  |  | #DIV/0! |  | 100 | NA | FALSE |  | pending
2026-06-09 | OLD03 | SV136.12 | PQ3-Week2 | FALSE | 12-2-036 | Building 12 | CIP 1 | PW | 2026-06-10 |  |  |  | #DIV/0! |  | 100 | NA | FALSE |  | pending
2026-06-09 | OLD04 | SV136.07 | PQ3-Week2 | FALSE | 12-2-034 | Building 12 | SYRUP PREPARATION | PW | 2026-06-10 |  |  |  | #DIV/0! |  | 100 | NA | FALSE |  | pending
2026-06-09 | OLD05 | SV136.06 | PQ3-Week2 | FALSE | 12-2-034 | Building 12 | SYRUP PREPARATION | PW | 2026-06-10 |  |  |  | #DIV/0! |  | 100 | NA | FALSE |  | pending
2026-06-09 | OLD12 | SV136.03 | PQ3-Week2 | FALSE | 12-2-032 | Building 12 | CAMPHORATED OPIUM TINCTURE | PW | 2026-06-10 |  |  |  | #DIV/0! |  | 100 | NA | FALSE |  | pending
2026-06-09 | OLD13 | SV136.05 | PQ3-Week2 | FALSE | 12-2-032 | Building 12 | CAMPHORATED OPIUM TINCTURE | PW | 2026-06-10 |  |  |  | #DIV/0! |  | 100 | NA | FALSE |  | pending
2026-06-09 | OLD14 | SV136.04 | PQ3-Week2 | FALSE | 12-2-030 | Building 12 | OPIUM TINCTURE | PW | 2026-06-10 |  |  |  | #DIV/0! |  | 100 | NA | FALSE |  | pending
2026-06-09 | OLD15 | DV136.02 | PQ3-Week2 | FALSE | 12-2-028 | Building 12 | ALCOHOL STORAGE | PW | 2026-06-10 |  |  |  | #DIV/0! |  | 100 | NA | FALSE |  | pending
2026-06-09 | OLD31 | DV136.07 | PQ3-Week2 | FALSE | 12-3-039 | Building 12 | INSTRUMENT 7 | PW | 2026-06-10 |  |  |  | #DIV/0! |  | 100 | NA | FALSE |  | pending
2026-06-12 | GOSD06 | SV113.01 | PQ3-Week2 | FALSE | WATER SYSTEM (B10) | Building 10 | After Storage tank (B10) | PW | 2026-06-13 |  |  |  | #DIV/0! |  | 100 | NA | FALSE |  | pending
2026-06-12 | GOSD07 | SV115.02 | PQ3-Week2 | FALSE | WATER SYSTEM (B10) | Building 10 | After UV (B10) | PW | 2026-06-13 |  |  |  | #DIV/0! |  | 100 | NA | FALSE |  | pending
2026-06-12 | GOSD08 | SV117.01 | PQ3-Week2 | FALSE | WATER SYSTEM (B10) | Building 10 | Return loop (B10) | PW | 2026-06-13 |  |  |  | #DIV/0! |  | 100 | NA | FALSE |  | pending
2026-06-12 | OSD22 | SV116.05 | PQ3-Week2 | FALSE | 10-3-062 | Building 10 | COATING ROOM-3 | PW | 2026-06-13 |  |  |  | #DIV/0! |  | 100 | NA | FALSE |  | pending
2026-06-12 | OSD23 | SV116.04 | PQ3-Week2 | FALSE | 10-3-061 | Building 10 | COATING ROOM-2 | PW | 2026-06-13 |  |  |  | #DIV/0! |  | 100 | NA | FALSE |  | pending
2026-06-12 | OSD24 | DV116.09 | PQ3-Week2 | FALSE | 10-3-060 | Building 10 | COATING SOLUTION PREP.-2 | PW | 2026-06-13 |  |  |  | #DIV/0! |  | 100 | NA | FALSE |  | pending
2026-06-12 | OSD25 | DV116.08 | PQ3-Week2 | FALSE | 10-3-059 | Building 10 | COATING SOLUTION PREP.-1 | PW | 2026-06-13 |  |  |  | #DIV/0! |  | 100 | NA | FALSE |  | pending
2026-06-12 | OSD26 | SV116.03 | PQ3-Week2 | FALSE | 10-3-058 | Building 10 | COATING ROOM-1 | PW | 2026-06-13 |  |  |  | #DIV/0! |  | 100 | NA | FALSE |  | pending
2026-06-12 | OSD29 | SV116.08 | PQ3-Week2 | FALSE | 10-3-067 | Building 10 | COATING ROOM-6 | PW | 2026-06-13 |  |  |  | #DIV/0! |  | 100 | NA | FALSE |  | pending
2026-06-12 | OSD30 | DV116.11 | PQ3-Week2 | FALSE | 10-3-066 | Building 10 | COATING SOLUTION PREP.-4 | PW | 2026-06-13 |  |  |  | #DIV/0! |  | 100 | NA | FALSE |  | pending
2026-06-12 | OSD31 | DV116.10 | PQ3-Week2 | FALSE | 10-3-065 | Building 10 | COATING SOLUTION PREP.-3 | PW | 2026-06-13 |  |  |  | #DIV/0! |  | 100 | NA | FALSE |  | pending
2026-06-12 | OSD32 | SV116.07 | PQ3-Week2 | FALSE | 10-3-064 | Building 10 | COATING ROOM-5 | PW | 2026-06-13 |  |  |  | #DIV/0! |  | 100 | NA | FALSE |  | pending
2026-06-12 | OSD33 | SV116.06 | PQ3-Week2 | FALSE | 10-3-063 | Building 10 | COATING ROOM-4 | PW | 2026-06-13 |  |  |  | #DIV/0! |  | 100 | NA | FALSE |  | pending
2026-06-12 | OSD36 | DV116.03 | PQ3-Week2 | FALSE | 10-2-034 | Building 10 | SAMPLE PREPARATION | PW | 2026-06-13 |  |  |  | #DIV/0! |  | 100 | NA | FALSE |  | pending
2026-06-12 | OSD37 | DV116.06 | PQ3-Week2 | FALSE | 10-2-034 | Building 10 | SAMPLE PREPARATION | PW | 2026-06-13 |  |  |  | #DIV/0! |  | 100 | NA | FALSE |  | pending
2026-06-12 | OSD38 | DV116.07 | PQ3-Week2 | FALSE | 10-2-032 | Building 10 | GLASS-WARE WASHING | PW | 2026-06-13 |  |  |  | #DIV/0! |  | 100 | NA | FALSE |  | pending
2026-06-12 | OSD39 | DV116.05 | PQ3-Week2 | FALSE | 10-2-032 | Building 10 | GLASS-WARE WASHING | PW | 2026-06-13 |  |  |  | #DIV/0! |  | 100 | NA | FALSE |  | pending
2026-06-12 | OSD40 | DV116.04 | PQ3-Week2 | FALSE | 10-2-037 | Building 10 | SKID FOR BIN WASHING-1 | PW | 2026-06-13 |  |  |  | #DIV/0! |  | 100 | NA | FALSE |  | pending
Formulas:
performedDate = [samplingDate]+1

## Backup wfi-pus
samplingDate | samplingPoint | samplingTag | recordStatus | worksheetCreate | noLocation | building | location | waterType | performedDate | determinedDate | result1 | resultAvg | comment | criteria | statusResult | Exclude | worksheet No. | status | syncStatus
2026-01-05 | GWFI01 | V12-4 | Pre PQ3/WFI | TRUE | 16-2-010 | Building 16 | AFTER WFI GENERATOR | WFI | 2026-01-06 | 2026-01-09 | 0 | 0 | NA | 10 | PASSED | FALSE | WP-26-0001 | complete | pending
2026-01-05 | GWFI02 | SV213.01 | Pre PQ3/WFI | TRUE | 16-2-010 | Building 16 | AFTER STORAGE TANK | WFI | 2026-01-06 | 2026-01-09 | 0 | 0 | NA | 10 | PASSED | FALSE | WP-26-0001 | complete | pending
2026-01-05 | GWFI03 | SV217.01 | Pre PQ3/WFI | TRUE | 16-2-010 | Building 16 | RETURN LOOP | WFI | 2026-01-06 | 2026-01-09 | 0 | 0 | NA | 10 | PASSED | FALSE | WP-26-0001 | complete | pending
2026-01-05 | WFI07 | SV216.02 | Pre PQ3/WFI | TRUE | 16-1-098 | Building 16 | CIP/SIP | WFI | 2026-01-06 | 2026-01-09 | 0 | 0 | NA | 10 | PASSED | FALSE | WP-26-0001 | complete | pending
2026-01-05 | WFI08 | SV216.04 | Pre PQ3/WFI | TRUE | 16-1-098 | Building 16 | CIP/SIP | WFI | 2026-01-06 | 2026-01-09 | 0 | 0 | NA | 10 | PASSED | FALSE | WP-26-0001 | complete | pending
2026-01-06 | GWFI01 | V12-4 | Pre PQ3/WFI | TRUE | 16-2-010 | Building 16 | AFTER WFI GENERATOR | WFI | 2026-01-08 | 2026-01-12 | 0 | 0 | NA | 10 | PASSED | FALSE | WP-26-0002 | complete | pending
2026-01-06 | GWFI03 | SV217.01 | Pre PQ3/WFI | TRUE | 16-2-010 | Building 16 | RETURN LOOP | WFI | 2026-01-08 | 2026-01-12 | 0 | 0 | NA | 10 | PASSED | FALSE | WP-26-0002 | complete | pending
2026-01-06 | WFI03 | SV216.03 | Pre PQ3/WFI | TRUE | 16-1-096 | Building 16 | WASHING/TUNNEL-02 | WFI | 2026-01-08 | 2026-01-12 | 0 | 0 | NA | 10 | PASSED | FALSE | WP-26-0002 | complete | pending
2026-01-06 | WFI04 | POU HE216.03 | Pre PQ3/WFI | TRUE | 16-1-082 | Building 16 | WASHING | WFI | 2026-01-08 | 2026-01-12 | 0 | 0 | NA | 10 | PASSED | FALSE | WP-26-0002 | complete | pending
2026-01-06 | WFI05 | SV216.06 | Pre PQ3/WFI | TRUE | 16-1-082 | Building 16 | WASHING | WFI | 2026-01-08 | 2026-01-12 | 0 | 0 | NA | 10 | PASSED | FALSE | WP-26-0002 | complete | pending
2026-01-07 | GWFI01 | V12-4 | Pre PQ3/WFI | TRUE | 16-2-010 | Building 16 | AFTER WFI GENERATOR | WFI | 2026-01-08 | 2026-01-12 | 0 | 0 | NA | 10 | PASSED | FALSE | WP-26-0003 | complete | pending
2026-01-07 | GWFI03 | SV217.01 | Pre PQ3/WFI | TRUE | 16-2-010 | Building 16 | RETURN LOOP | WFI | 2026-01-08 | 2026-01-12 | 0 | 0 | NA | 10 | PASSED | FALSE | WP-26-0003 | complete | pending
2026-01-07 | WFI06 | SV216.05 | Pre PQ3/WFI | TRUE | 16-1-110 | Building 16 | DISINFECTANT PREPARATION | WFI | 2026-01-08 | 2026-01-12 | 0 | 0 | NA | 10 | PASSED | FALSE | WP-26-0003 | complete | pending
2026-01-07 | WFI09 | SV216.10 | Pre PQ3/WFI | TRUE | 16-1-105 | Building 16 | WASHING/TUNNEL-01 | WFI | 2026-01-08 | 2026-01-12 | 0 | 0 | NA | 10 | PASSED | FALSE | WP-26-0003 | complete | pending
2026-01-08 | GWFI01 | V12-4 | Pre PQ3/WFI | TRUE | 16-2-010 | Building 16 | AFTER WFI GENERATOR | WFI | 2026-01-10 | 2026-01-13 | 0 | 0 | NA | 10 | PASSED | FALSE | WP-26-0004 | complete | pending
2026-01-08 | GWFI03 | SV217.01 | Pre PQ3/WFI | TRUE | 16-2-010 | Building 16 | RETURN LOOP | WFI | 2026-01-10 | 2026-01-13 | 0 | 0 | NA | 10 | PASSED | FALSE | WP-26-0004 | complete | pending
2026-01-08 | WFI01 | POU HE216.01 | Pre PQ3/WFI | TRUE | 16-1-107 | Building 16 | COMPOUNDING-01 | WFI | 2026-01-10 | 2026-01-13 | 0 | 0 | NA | 10 | PASSED | FALSE | WP-26-0004 | complete | pending
2026-01-08 | WFI01 | POU HE216.01 | Pre PQ3/WFI | TRUE | 16-1-107 | Building 16 | COMPOUNDING-01 | WFI | 2026-01-10 | 2026-01-13 | 0 | 0 | ข้างถัง | 10 | PASSED | FALSE | WP-26-0004 | complete | pending
2026-01-08 | WFI02 | POU HE216.02 | Pre PQ3/WFI | TRUE | 16-1-107 | Building 16 | COMPOUNDING-01 | WFI | 2026-01-10 | 2026-01-13 | 1 | 1 | NA | 10 | PASSED | FALSE | WP-26-0004 | complete | pending
2026-01-08 | WFI02 | POU HE216.02 | Pre PQ3/WFI | TRUE | 16-1-107 | Building 16 | COMPOUNDING-01 | WFI | 2026-01-10 | 2026-01-13 | 11 | 11 | ข้างถัง | 10 | NOT-PASSED | FALSE | WP-26-0004 | complete | pending
2026-01-09 | GWFI01 | V12-4 | Pre PQ3/WFI | TRUE | 16-2-010 | Building 16 | AFTER WFI GENERATOR | WFI | 2026-01-10 | 2026-01-13 | 0 | 0 | NA | 10 | PASSED | FALSE | WP-26-0005 | complete | pending
2026-01-09 | GWFI03 | SV217.01 | Pre PQ3/WFI | TRUE | 16-2-010 | Building 16 | RETURN LOOP | WFI | 2026-01-10 | 2026-01-13 | 0 | 0 | NA | 10 | PASSED | FALSE | WP-26-0005 | complete | pending
2026-01-09 | WFI10 | POU HE216.04 | Pre PQ3/WFI | TRUE | 16-1-114 | Building 16 | COMPOUNDING-02 | WFI | 2026-01-10 | 2026-01-13 | 0 | 0 | NA | 10 | PASSED | FALSE | WP-26-0005 | complete | pending
2026-01-09 | WFI10 | POU HE216.04 | Pre PQ3/WFI | TRUE | 16-1-114 | Building 16 | COMPOUNDING-02 | WFI | 2026-01-10 | 2026-01-13 | 9999 | 9999 | ข้างถัง | 10 | NOT-PASSED | FALSE | WP-26-0005 | complete | pending
2026-01-09 | WFI11 | POU HE216.05 | Pre PQ3/WFI | TRUE | 16-1-114 | Building 16 | COMPOUNDING-02 | WFI | 2026-01-10 | 2026-01-13 | 63 | 63 | NA | 10 | NOT-PASSED | FALSE | WP-26-0005 | complete | pending
2026-01-09 | WFI11 | POU HE216.05 | Pre PQ3/WFI | TRUE | 16-1-114 | Building 16 | COMPOUNDING-02 | WFI | 2026-01-10 | 2026-01-13 | 2 | 2 | ข้างถัง | 10 | PASSED | FALSE | WP-26-0005 | complete | pending
2026-01-19 | GWFI01 | V12-4 | Pre PQ3/WFI | TRUE | 16-2-010 | Building 16 | AFTER WFI GENERATOR | WFI | 2026-01-20 | 2026-01-23 | 0 | 0 | NA | 10 | PASSED | FALSE | WP-26-0006 | complete | pending
2026-01-19 | GWFI02 | SV213.01 | Pre PQ3/WFI | TRUE | 16-2-010 | Building 16 | AFTER STORAGE TANK | WFI | 2026-01-20 | 2026-01-23 | 0 | 0 | NA | 10 | PASSED | FALSE | WP-26-0006 | complete | pending
2026-01-19 | GWFI03 | SV217.01 | Pre PQ3/WFI | TRUE | 16-2-010 | Building 16 | RETURN LOOP | WFI | 2026-01-20 | 2026-01-23 | 0 | 0 | NA | 10 | PASSED | FALSE | WP-26-0006 | complete | pending
2026-01-19 | WFI07 | SV216.02 | Pre PQ3/WFI | TRUE | 16-1-098 | Building 16 | CIP/SIP | WFI | 2026-01-20 | 2026-01-23 | 0 | 0 | NA | 10 | PASSED | FALSE | WP-26-0006 | complete | pending
2026-01-19 | WFI08 | SV216.04 | Pre PQ3/WFI | TRUE | 16-1-098 | Building 16 | CIP/SIP | WFI | 2026-01-20 | 2026-01-23 | 0 | 0 | NA | 10 | PASSED | FALSE | WP-26-0006 | complete | pending
2026-01-20 | GWFI01 | V12-4 | Pre PQ3/WFI | TRUE | 16-2-010 | Building 16 | AFTER WFI GENERATOR | WFI | 2026-01-22 | 2026-01-25 | 0 | 0 | NA | 10 | PASSED | FALSE | WP-26-0007 | complete | pending
2026-01-20 | GWFI03 | SV217.01 | Pre PQ3/WFI | TRUE | 16-2-010 | Building 16 | RETURN LOOP | WFI | 2026-01-22 | 2026-01-25 | 0 | 0 | NA | 10 | PASSED | FALSE | WP-26-0007 | complete | pending
2026-01-20 | WFI03 | SV216.03 | Pre PQ3/WFI | TRUE | 16-1-096 | Building 16 | WASHING/TUNNEL-02 | WFI | 2026-01-22 | 2026-01-25 | 0 | 0 | NA | 10 | PASSED | FALSE | WP-26-0007 | complete | pending
2026-01-20 | WFI04 | POU HE216.03 | Pre PQ3/WFI | TRUE | 16-1-082 | Building 16 | WASHING | WFI | 2026-01-22 | 2026-01-25 | 0 | 0 | NA | 10 | PASSED | FALSE | WP-26-0007 | complete | pending
2026-01-20 | WFI05 | SV216.06 | Pre PQ3/WFI | TRUE | 16-1-082 | Building 16 | WASHING | WFI | 2026-01-22 | 2026-01-25 | 0 | 0 | NA | 10 | PASSED | FALSE | WP-26-0007 | complete | pending
2026-01-21 | GWFI01 | V12-4 | Pre PQ3/WFI | TRUE | 16-2-010 | Building 16 | AFTER WFI GENERATOR | WFI | 2026-01-22 | 2026-01-25 | 0 | 0 | NA | 10 | PASSED | FALSE | WP-26-0008 | complete | pending
2026-01-21 | GWFI03 | SV217.01 | Pre PQ3/WFI | TRUE | 16-2-010 | Building 16 | RETURN LOOP | WFI | 2026-01-22 | 2026-01-25 | 0 | 0 | NA | 10 | PASSED | FALSE | WP-26-0008 | complete | pending
2026-01-21 | WFI06 | SV216.05 | Pre PQ3/WFI | TRUE | 16-1-110 | Building 16 | DISINFECTANT PREPARATION | WFI | 2026-01-22 | 2026-01-25 | 0 | 0 | NA | 10 | PASSED | FALSE | WP-26-0008 | complete | pending
2026-01-21 | WFI09 | SV216.10 | Pre PQ3/WFI | TRUE | 16-1-105 | Building 16 | WASHING/TUNNEL-01 | WFI | 2026-01-22 | 2026-01-25 | 0 | 0 | NA | 10 | PASSED | FALSE | WP-26-0008 | complete | pending
2026-01-22 | GWFI01 | V12-4 | Pre PQ3/WFI | TRUE | 16-2-010 | Building 16 | AFTER WFI GENERATOR | WFI | 2026-01-24 | 2026-01-27 | 0 | 0 | NA | 10 | PASSED | FALSE | WT-26-0082 | complete | synced
2026-01-22 | GWFI03 | SV217.01 | Pre PQ3/WFI | TRUE | 16-2-010 | Building 16 | RETURN LOOP | WFI | 2026-01-24 | 2026-01-27 | 0 | 0 | NA | 10 | PASSED | FALSE | WT-26-0082 | complete | synced
2026-01-22 | WFI01 | POU HE216.01 | Pre PQ3/WFI | TRUE | 16-1-107 | Building 16 | COMPOUNDING-01 | WFI | 2026-01-24 | 2026-01-27 | 0 | 0 | NA | 10 | PASSED | FALSE | WT-26-0082 | complete | synced
2026-01-22 | WFI01 | POU HE216.01 | Pre PQ3/WFI | TRUE | 16-1-107 | Building 16 | COMPOUNDING-01 | WFI | 2026-01-24 | 2026-01-27 | 0 | 0 | ข้างถัง | 10 | PASSED | FALSE | WT-26-0082 | complete | synced
2026-01-22 | WFI02 | POU HE216.02 | Pre PQ3/WFI | TRUE | 16-1-107 | Building 16 | COMPOUNDING-01 | WFI | 2026-01-24 | 2026-01-27 | 0 | 0 | NA | 10 | PASSED | FALSE | WT-26-0082 | complete | synced
2026-01-22 | WFI02 | POU HE216.02 | Pre PQ3/WFI | TRUE | 16-1-107 | Building 16 | COMPOUNDING-01 | WFI | 2026-01-24 | 2026-01-27 | 22 | 22 | ข้างถัง | 10 | NOT-PASSED | FALSE | WT-26-0082 | complete | synced
2026-01-23 | GWFI01 | V12-4 | Pre PQ3/WFI | TRUE | 16-2-010 | Building 16 | AFTER WFI GENERATOR | WFI | 2026-01-24 | 2026-01-27 | 0 | 0 | NA | 10 | PASSED | FALSE | WP-26-0010 | complete | pending
2026-01-23 | GWFI03 | SV217.01 | Pre PQ3/WFI | TRUE | 16-2-010 | Building 16 | RETURN LOOP | WFI | 2026-01-24 | 2026-01-27 | 0 | 0 | NA | 10 | PASSED | FALSE | WP-26-0010 | complete | pending
2026-01-23 | WFI10 | POU HE216.04 | Pre PQ3/WFI | TRUE | 16-1-114 | Building 16 | COMPOUNDING-02 | WFI | 2026-01-24 | 2026-01-27 | 0 | 0 | NA | 10 | PASSED | FALSE | WP-26-0010 | complete | pending
2026-01-23 | WFI10 | POU HE216.04 | Pre PQ3/WFI | TRUE | 16-1-114 | Building 16 | COMPOUNDING-02 | WFI | 2026-01-24 | 2026-01-27 | 13 | 13 | ข้างถัง | 10 | NOT-PASSED | FALSE | WP-26-0010 | complete | pending
2026-01-23 | WFI11 | POU HE216.05 | Pre PQ3/WFI | TRUE | 16-1-114 | Building 16 | COMPOUNDING-02 | WFI | 2026-01-24 | 2026-01-27 | 0 | 0 | NA | 10 | PASSED | FALSE | WP-26-0010 | complete | pending
2026-01-23 | WFI11 | POU HE216.05 | Pre PQ3/WFI | TRUE | 16-1-114 | Building 16 | COMPOUNDING-02 | WFI | 2026-01-24 | 2026-01-27 | 0 | 0 | ข้างถัง | 10 | PASSED | FALSE | WP-26-0010 | complete | pending
2026-02-02 | GWFI01 | V12-4 | PQ3-Day1 | TRUE | 16-2-010 | Building 16 | AFTER WFI GENERATOR | WFI | 2026-02-03 | 2026-02-06 | 0 | 0 | NA | 10 | PASSED | FALSE | WP-26-0009 | complete | pending
2026-02-02 | GWFI02 | SV213.01 | PQ3-Day1 | TRUE | 16-2-010 | Building 16 | AFTER STORAGE TANK | WFI | 2026-02-03 | 2026-02-06 | 0 | 0 | NA | 10 | PASSED | FALSE | WP-26-0009 | complete | pending
2026-02-02 | GWFI03 | SV217.01 | PQ3-Day1 | TRUE | 16-2-010 | Building 16 | RETURN LOOP | WFI | 2026-02-03 | 2026-02-06 | 0 | 0 | NA | 10 | PASSED | FALSE | WP-26-0009 | complete | pending
2026-02-02 | WFI07 | SV216.02 | PQ3-Day1 | TRUE | 16-1-098 | Building 16 | CIP/SIP | WFI | 2026-02-03 | 2026-02-06 | 0 | 0 | NA | 10 | PASSED | FALSE | WP-26-0009 | complete | pending
2026-02-02 | WFI08 | SV216.04 | PQ3-Day1 | TRUE | 16-1-098 | Building 16 | CIP/SIP | WFI | 2026-02-03 | 2026-02-06 | 0 | 0 | NA | 10 | PASSED | FALSE | WP-26-0009 | complete | pending
2026-02-03 | WFI03 | SV216.03 | PQ3-Day2 | TRUE | 16-1-096 | Building 16 | WASHING/TUNNEL-02 | WFI | 2026-02-05 | 2026-02-09 | 0 | 0 | NA | 10 | PASSED | FALSE | WP-26-0012 | complete | pending
2026-02-03 | WFI04 | POU HE216.03 | PQ3-Day2 | TRUE | 16-1-082 | Building 16 | WASHING | WFI | 2026-02-05 | 2026-02-09 | 0 | 0 | NA | 10 | PASSED | FALSE | WP-26-0012 | complete | pending
2026-02-03 | WFI05 | SV216.06 | PQ3-Day2 | TRUE | 16-1-082 | Building 16 | WASHING | WFI | 2026-02-05 | 2026-02-09 | 0 | 0 | NA | 10 | PASSED | FALSE | WP-26-0012 | complete | pending
2026-02-04 | WFI09 | SV216.10 | PQ3-Day3 | TRUE | 16-1-105 | Building 16 | WASHING/TUNNEL-01 | WFI | 2026-02-05 | 2026-02-09 | 0 | 0 | NA | 10 | PASSED | FALSE | WP-26-0013 | complete | pending
2026-02-04 | WFI10 | POU HE216.04 | PQ3-Day3 | TRUE | 16-1-114 | Building 16 | COMPOUNDING-02 | WFI | 2026-02-05 | 2026-02-09 | 0 | 0 | NA | 10 | PASSED | FALSE | WP-26-0013 | complete | pending
2026-02-04 | WFI11 | POU HE216.05 | PQ3-Day3 | TRUE | 16-1-114 | Building 16 | COMPOUNDING-02 | WFI | 2026-02-05 | 2026-02-09 | 9 | 9 | NA | 10 | PASSED | FALSE | WP-26-0013 | complete | pending
2026-02-05 | WFI01 | POU HE216.01 | PQ3-Day4 | TRUE | 16-1-107 | Building 16 | COMPOUNDING-01 | WFI | 2026-02-07 | 2026-02-10 | 0 | 0 | NA | 10 | PASSED | FALSE | WP-26-0014 | complete | pending
2026-02-05 | WFI02 | POU HE216.02 | PQ3-Day4 | TRUE | 16-1-107 | Building 16 | COMPOUNDING-01 | WFI | 2026-02-07 | 2026-02-10 | 0 | 0 | NA | 10 | PASSED | FALSE | WP-26-0014 | complete | pending
2026-02-06 | WFI06 | SV216.05 | PQ3-Day5 | TRUE | 16-1-110 | Building 16 | DISINFECTANT PREPARATION | WFI | 2026-02-07 | 2026-02-10 | 0 | 0 | NA | 10 | PASSED | FALSE | WP-26-0015 | complete | pending
2026-02-09 | GWFI01 | V12-4 | PQ3-Day1 | TRUE | 16-2-010 | Building 16 | AFTER WFI GENERATOR | WFI | 2026-02-10 | 2026-02-13 | 0 | 0 | NA | 10 | PASSED | FALSE | WP-26-0016 | complete | pending
2026-02-09 | GWFI02 | SV213.01 | PQ3-Day1 | TRUE | 16-2-010 | Building 16 | AFTER STORAGE TANK | WFI | 2026-02-10 | 2026-02-13 | 0 | 0 | NA | 10 | PASSED | FALSE | WP-26-0016 | complete | pending
2026-02-09 | GWFI03 | SV217.01 | PQ3-Day1 | TRUE | 16-2-010 | Building 16 | RETURN LOOP | WFI | 2026-02-10 | 2026-02-13 | 0 | 0 | NA | 10 | PASSED | FALSE | WP-26-0016 | complete | pending
2026-02-09 | WFI08 | SV216.04 | PQ3-Day1 | TRUE | 16-1-098 | Building 16 | CIP/SIP | WFI | 2026-02-10 | 2026-02-13 | 0 | 0 | NA | 10 | PASSED | FALSE | WP-26-0016 | complete | pending
2026-02-10 | WFI03 | SV216.03 | PQ3-Day2 | TRUE | 16-1-096 | Building 16 | WASHING/TUNNEL-02 | WFI | 2026-02-12 | 2026-02-16 | 0 | 0 | NA | 10 | PASSED | FALSE | WP-26-0017 | complete | pending
2026-02-10 | WFI04 | POU HE216.03 | PQ3-Day2 | TRUE | 16-1-082 | Building 16 | WASHING | WFI | 2026-02-12 | 2026-02-16 | 0 | 0 | NA | 10 | PASSED | FALSE | WP-26-0017 | complete | pending
2026-02-10 | WFI05 | SV216.06 | PQ3-Day2 | TRUE | 16-1-082 | Building 16 | WASHING | WFI | 2026-02-12 | 2026-02-16 | 0 | 0 | NA | 10 | PASSED | FALSE | WP-26-0017 | complete | pending
2026-02-11 | WFI07 | SV216.02 | PQ3-Day3 | TRUE | 16-1-098 | Building 16 | CIP/SIP | WFI | 2026-02-12 | 2026-02-16 | 0 | 0 | NA | 10 | PASSED | FALSE | WP-26-0018 | complete | pending
2026-02-11 | WFI10 | POU HE216.04 | PQ3-Day3 | TRUE | 16-1-114 | Building 16 | COMPOUNDING-02 | WFI | 2026-02-12 | 2026-02-16 | 0 | 0 | NA | 10 | PASSED | FALSE | WP-26-0018 | complete | pending
2026-02-11 | WFI11 | POU HE216.05 | PQ3-Day3 | TRUE | 16-1-114 | Building 16 | COMPOUNDING-02 | WFI | 2026-02-12 | 2026-02-16 | 0 | 0 | NA | 10 | PASSED | FALSE | WP-26-0018 | complete | pending
2026-02-12 | WFI01 | POU HE216.01 | PQ3-Day4 | TRUE | 16-1-107 | Building 16 | COMPOUNDING-01 | WFI | 2026-02-14 | 2026-02-17 | 0 | 0 | NA | 10 | PASSED | FALSE | WP-26-0019 | complete | pending
2026-02-12 | WFI02 | POU HE216.02 | PQ3-Day4 | TRUE | 16-1-107 | Building 16 | COMPOUNDING-01 | WFI | 2026-02-14 | 2026-02-17 | 0 | 0 | NA | 10 | PASSED | FALSE | WP-26-0019 | complete | pending
2026-02-13 | WFI06 | SV216.05 | PQ3-Day5 | TRUE | 16-1-110 | Building 16 | DISINFECTANT PREPARATION | WFI | 2026-02-14 | 2026-02-17 | 0 | 0 | NA | 10 | PASSED | FALSE | WP-26-0020 | complete | pending
2026-02-13 | WFI09 | SV216.10 | PQ3-Day5 | TRUE | 16-1-105 | Building 16 | WASHING/TUNNEL-01 | WFI | 2026-02-14 | 2026-02-17 | 0 | 0 | NA | 10 | PASSED | FALSE | WP-26-0020 | complete | pending
2026-02-16 | GWFI01 | V12-4 | PQ3-Day1 | TRUE | 16-2-010 | Building 16 | AFTER WFI GENERATOR | WFI | 2026-02-18 | 2026-02-21 | 0 | 0 | NA | 10 | PASSED | FALSE | WP-26-0021 | complete | pending
2026-02-16 | GWFI02 | SV213.01 | PQ3-Day1 | TRUE | 16-2-010 | Building 16 | AFTER STORAGE TANK | WFI | 2026-02-18 | 2026-02-21 | 0 | 0 | NA | 10 | PASSED | FALSE | WP-26-0021 | complete | pending
2026-02-16 | GWFI03 | SV217.01 | PQ3-Day1 | TRUE | 16-2-010 | Building 16 | RETURN LOOP | WFI | 2026-02-18 | 2026-02-21 | 0 | 0 | NA | 10 | PASSED | FALSE | WP-26-0021 | complete | pending
2026-02-16 | WFI07 | SV216.02 | PQ3-Day1 | TRUE | 16-1-098 | Building 16 | CIP/SIP | WFI | 2026-02-18 | 2026-02-21 | 0 | 0 | NA | 10 | PASSED | FALSE | WP-26-0021 | complete | pending
2026-02-16 | WFI08 | SV216.04 | PQ3-Day1 | TRUE | 16-1-098 | Building 16 | CIP/SIP | WFI | 2026-02-18 | 2026-02-21 | 0 | 0 | NA | 10 | PASSED | FALSE | WP-26-0021 | complete | pending
2026-02-17 | WFI03 | SV216.03 | PQ3-Day2 | TRUE | 16-1-096 | Building 16 | WASHING/TUNNEL-02 | WFI | 2026-02-18 | 2026-02-21 | 0 | 0 | NA | 10 | PASSED | FALSE | WP-26-0022 | complete | pending
2026-02-17 | WFI04 | POU HE216.03 | PQ3-Day2 | TRUE | 16-1-082 | Building 16 | WASHING | WFI | 2026-02-18 | 2026-02-21 | 0 | 0 | NA | 10 | PASSED | FALSE | WP-26-0022 | complete | pending
2026-02-17 | WFI05 | SV216.06 | PQ3-Day2 | TRUE | 16-1-082 | Building 16 | WASHING | WFI | 2026-02-18 | 2026-02-21 | 0 | 0 | NA | 10 | PASSED | FALSE | WP-26-0022 | complete | pending
2026-02-18 | WFI10 | POU HE216.04 | PQ3-Day3 | TRUE | 16-1-114 | Building 16 | COMPOUNDING-02 | WFI | 2026-02-20 | 2026-02-23 | 0 | 0 | NA | 10 | PASSED | FALSE | WP-26-0023 | complete | pending
2026-02-18 | WFI11 | POU HE216.05 | PQ3-Day3 | TRUE | 16-1-114 | Building 16 | COMPOUNDING-02 | WFI | 2026-02-20 | 2026-02-23 | 0 | 0 | NA | 10 | PASSED | FALSE | WP-26-0023 | complete | pending
2026-02-19 | WFI01 | POU HE216.01 | PQ3-Day4 | TRUE | 16-1-107 | Building 16 | COMPOUNDING-01 | WFI | 2026-02-20 | 2026-02-23 | 0 | 0 | NA | 10 | PASSED | FALSE | WP-26-0024 | complete | pending
2026-02-19 | WFI02 | POU HE216.02 | PQ3-Day4 | TRUE | 16-1-107 | Building 16 | COMPOUNDING-01 | WFI | 2026-02-20 | 2026-02-23 | 0 | 0 | NA | 10 | PASSED | FALSE | WP-26-0024 | complete | pending
2026-02-20 | WFI06 | SV216.05 | PQ3-Day5 | TRUE | 16-1-110 | Building 16 | DISINFECTANT PREPARATION | WFI | 2026-02-21 | 2026-02-24 | 0 | 0 | NA | 10 | PASSED | FALSE | WP-26-0025 | complete | pending
2026-02-20 | WFI09 | SV216.10 | PQ3-Day5 | TRUE | 16-1-105 | Building 16 | WASHING/TUNNEL-01 | WFI | 2026-02-21 | 2026-02-24 | 0 | 0 | NA | 10 | PASSED | FALSE | WP-26-0025 | complete | pending
2026-02-23 | GWFI01 | V12-4 | PQ3-Day1 | TRUE | 16-2-010 | Building 16 | AFTER WFI GENERATOR | WFI | 2026-02-24 | 2026-03-02 | 0 | 0 | NA | 10 | PASSED | FALSE | WP-26-0030 | complete | pending
2026-02-23 | GWFI02 | SV213.01 | PQ3-Day1 | TRUE | 16-2-010 | Building 16 | AFTER STORAGE TANK | WFI | 2026-02-24 | 2026-03-02 | 0 | 0 | NA | 10 | PASSED | FALSE | WP-26-0030 | complete | pending
2026-02-23 | GWFI03 | SV217.01 | PQ3-Day1 | TRUE | 16-2-010 | Building 16 | RETURN LOOP | WFI | 2026-02-24 | 2026-03-02 | 0 | 0 | NA | 10 | PASSED | FALSE | WP-26-0030 | complete | pending
2026-02-23 | WFI07 | SV216.02 | PQ3-Day1 | TRUE | 16-1-098 | Building 16 | CIP/SIP | WFI | 2026-02-24 | 2026-03-02 | 0 | 0 | NA | 10 | PASSED | FALSE | WP-26-0030 | complete | pending
2026-02-23 | WFI08 | SV216.04 | PQ3-Day1 | TRUE | 16-1-098 | Building 16 | CIP/SIP | WFI | 2026-02-24 | 2026-03-02 | 0 | 0 | NA | 10 | PASSED | FALSE | WP-26-0030 | complete | pending
2026-02-24 | WFI03 | SV216.03 | PQ3-Day2 | TRUE | 16-1-096 | Building 16 | WASHING/TUNNEL-02 | WFI | 2026-02-26 | 2026-03-03 | 0 | 0 | NA | 10 | PASSED | FALSE | WP-26-0026 | complete | pending
2026-02-24 | WFI04 | POU HE216.03 | PQ3-Day2 | TRUE | 16-1-082 | Building 16 | WASHING | WFI | 2026-02-26 | 2026-03-03 | 0 | 0 | NA | 10 | PASSED | FALSE | WP-26-0026 | complete | pending
2026-02-24 | WFI05 | SV216.06 | PQ3-Day2 | TRUE | 16-1-082 | Building 16 | WASHING | WFI | 2026-02-26 | 2026-03-03 | 0 | 0 | NA | 10 | PASSED | FALSE | WP-26-0026 | complete | pending
2026-02-25 | WFI10 | POU HE216.04 | PQ3-Day3 | TRUE | 16-1-114 | Building 16 | COMPOUNDING-02 | WFI | 2026-02-26 | 2026-03-03 | 0 | 0 | NA | 10 | PASSED | FALSE | WP-26-0027 | complete | pending
2026-02-25 | WFI11 | POU HE216.05 | PQ3-Day3 | TRUE | 16-1-114 | Building 16 | COMPOUNDING-02 | WFI | 2026-02-26 | 2026-03-03 | 0 | 0 | NA | 10 | PASSED | FALSE | WP-26-0027 | complete | pending
2026-02-26 | WFI06 | SV216.05 | PQ3-Day4 | TRUE | 16-1-110 | Building 16 | DISINFECTANT PREPARATION | WFI | 2026-02-28 | 2026-03-03 | 0 | 0 | NA | 10 | PASSED | FALSE | WP-26-0028 | complete | pending
2026-02-26 | WFI09 | SV216.10 | PQ3-Day4 | TRUE | 16-1-105 | Building 16 | WASHING/TUNNEL-01 | WFI | 2026-02-28 | 2026-03-03 | 0 | 0 | NA | 10 | PASSED | FALSE | WP-26-0028 | complete | pending
2026-02-27 | WFI01 | POU HE216.01 | PQ3-Day5 | TRUE | 16-1-107 | Building 16 | COMPOUNDING-01 | WFI | 2026-02-28 | 2026-03-03 | 0 | 0 | NA | 10 | PASSED | FALSE | WP-26-0029 | complete | pending
2026-02-27 | WFI02 | POU HE216.02 | PQ3-Day5 | TRUE | 16-1-107 | Building 16 | COMPOUNDING-01 | WFI | 2026-02-28 | 2026-03-03 | 0 | 0 | NA | 10 | PASSED | FALSE | WP-26-0029 | complete | pending
2026-03-02 | GWFI01 | V12-4 | PQ3-Day1 | TRUE | 16-2-010 | Building 16 | AFTER WFI GENERATOR | WFI | 2026-03-03 | 2026-03-06 | 0 | 0 | NA | 10 | PASSED | FALSE | WP-26-0032 | complete | pending
2026-03-02 | GWFI02 | SV213.01 | PQ3-Day1 | TRUE | 16-2-010 | Building 16 | AFTER STORAGE TANK | WFI | 2026-03-03 | 2026-03-06 | 0 | 0 | NA | 10 | PASSED | FALSE | WP-26-0032 | complete | pending
2026-03-02 | GWFI03 | SV217.01 | PQ3-Day1 | TRUE | 16-2-010 | Building 16 | RETURN LOOP | WFI | 2026-03-03 | 2026-03-06 | 0 | 0 | NA | 10 | PASSED | FALSE | WP-26-0032 | complete | pending
2026-03-02 | WFI07 | SV216.02 | PQ3-Day1 | TRUE | 16-1-098 | Building 16 | CIP/SIP | WFI | 2026-03-03 | 2026-03-06 | 0 | 0 | NA | 10 | PASSED | FALSE | WP-26-0032 | complete | pending
2026-03-02 | WFI08 | SV216.04 | PQ3-Day1 | TRUE | 16-1-098 | Building 16 | CIP/SIP | WFI | 2026-03-03 | 2026-03-06 | 0 | 0 | NA | 10 | PASSED | FALSE | WP-26-0032 | complete | pending
2026-03-04 | WFI10 | POU HE216.04 | PQ3-Day2 | TRUE | 16-1-114 | Building 16 | COMPOUNDING-02 | WFI | 2026-03-05 | 2026-03-10 | 0 | 0 | NA | 10 | PASSED | FALSE | WP-26-0031 | complete | pending
2026-03-04 | WFI11 | POU HE216.05 | PQ3-Day2 | TRUE | 16-1-114 | Building 16 | COMPOUNDING-02 | WFI | 2026-03-05 | 2026-03-10 | 0 | 0 | NA | 10 | PASSED | FALSE | WP-26-0031 | complete | pending
2026-03-05 | WFI01 | POU HE216.01 | PQ3-Day3 | TRUE | 16-1-107 | Building 16 | COMPOUNDING-01 | WFI | 2026-03-07 | 2026-03-10 | 0 | 0 | NA | 10 | PASSED |  | WP-26-0046 | complete | pending
2026-03-05 | WFI02 | POU HE216.02 | PQ3-Day3 | TRUE | 16-1-107 | Building 16 | COMPOUNDING-01 | WFI | 2026-03-07 | 2026-03-10 | 0 | 0 | NA | 10 | PASSED | FALSE | WP-26-0046 | complete | pending
2026-03-06 | WFI03 | SV216.03 | PQ3-Day4 | TRUE | 16-1-096 | Building 16 | WASHING/TUNNEL-02 | WFI | 2026-03-07 | 2026-03-10 | 0 | 0 | NA | 10 | PASSED | FALSE | WP-26-0045 | complete | pending
2026-03-06 | WFI04 | POU HE216.03 | PQ3-Day4 | TRUE | 16-1-082 | Building 16 | WASHING | WFI | 2026-03-07 | 2026-03-10 | 0 | 0 | NA | 10 | PASSED | FALSE | WP-26-0045 | complete | pending
2026-03-06 | WFI05 | SV216.06 | PQ3-Day4 | TRUE | 16-1-082 | Building 16 | WASHING | WFI | 2026-03-07 | 2026-03-10 | 0 | 0 | NA | 10 | PASSED | FALSE | WP-26-0045 | complete | pending
2026-03-06 | WFI06 | SV216.05 | PQ3-Day4 | TRUE | 16-1-110 | Building 16 | DISINFECTANT PREPARATION | WFI | 2026-03-07 | 2026-03-10 | 0 | 0 | NA | 10 | PASSED | FALSE | WP-26-0045 | complete | pending
2026-03-06 | WFI09 | SV216.10 | PQ3-Day4 | TRUE | 16-1-105 | Building 16 | WASHING/TUNNEL-01 | WFI | 2026-03-07 | 2026-03-10 | 0 | 0 | NA | 10 | PASSED | FALSE | WP-26-0045 | complete | pending
2026-03-09 | GWFI02 | SV213.01 | Special | TRUE | 16-2-010 | Building 16 | AFTER STORAGE TANK | WFI | 2026-03-11 | 2026-03-14 | 0 | 0 | shutdown 36 hr. (ช.) | 10 | PASSED |  | WP-26-0033 | complete | pending
2026-03-09 | GWFI03 | SV217.01 | Special | TRUE | 16-2-010 | Building 16 | RETURN LOOP | WFI | 2026-03-11 | 2026-03-14 | 0 | 0 | shutdown 36 hr. (ช.) | 10 | PASSED |  | WP-26-0033 | complete | pending
2026-03-09 | GWFI01 | V12-4 | Special | TRUE | 16-2-010 | Building 16 | AFTER WFI GENERATOR | WFI | 2026-03-11 | 2026-03-14 | 0 | 0 | shutdown 36 hr. | 10 | PASSED |  | WP-26-0033 | complete | pending
2026-03-09 | GWFI02 | SV213.01 | Special | TRUE | 16-2-010 | Building 16 | AFTER STORAGE TANK | WFI | 2026-03-11 | 2026-03-14 | 0 | 0 | shutdown 36 hr. | 10 | PASSED |  | WP-26-0033 | complete | pending
2026-03-09 | GWFI03 | SV217.01 | Special | TRUE | 16-2-010 | Building 16 | RETURN LOOP | WFI | 2026-03-11 | 2026-03-14 | 0 | 0 | shutdown 36 hr. | 10 | PASSED |  | WP-26-0033 | complete | pending
2026-03-09 | WFI01 | POU HE216.01 | Special | TRUE | 16-1-107 | Building 16 | COMPOUNDING-01 | WFI | 2026-03-11 | 2026-03-14 | 0 | 0 | shutdown 36 hr. | 10 | PASSED |  | WP-26-0033 | complete | pending
2026-03-09 | WFI02 | POU HE216.02 | Special | TRUE | 16-1-107 | Building 16 | COMPOUNDING-01 | WFI | 2026-03-11 | 2026-03-14 | 0 | 0 | shutdown 36 hr. | 10 | PASSED |  | WP-26-0033 | complete | pending
2026-03-09 | WFI03 | SV216.03 | Special | TRUE | 16-1-096 | Building 16 | WASHING/TUNNEL-02 | WFI | 2026-03-11 | 2026-03-14 | 0 | 0 | shutdown 36 hr. | 10 | PASSED |  | WP-26-0033 | complete | pending
2026-03-09 | WFI04 | POU HE216.03 | Special | TRUE | 16-1-082 | Building 16 | WASHING | WFI | 2026-03-11 | 2026-03-14 | 0 | 0 | shutdown 36 hr. | 10 | PASSED |  | WP-26-0033 | complete | pending
2026-03-09 | WFI05 | SV216.06 | Special | TRUE | 16-1-082 | Building 16 | WASHING | WFI | 2026-03-11 | 2026-03-14 | 0 | 0 | shutdown 36 hr. | 10 | PASSED |  | WP-26-0033 | complete | pending
2026-03-09 | WFI06 | SV216.05 | Special | TRUE | 16-1-110 | Building 16 | DISINFECTANT PREPARATION | WFI | 2026-03-11 | 2026-03-14 | 0 | 0 | shutdown 36 hr. | 10 | PASSED |  | WP-26-0033 | complete | pending
2026-03-09 | WFI07 | SV216.02 | Special | TRUE | 16-1-098 | Building 16 | CIP/SIP | WFI | 2026-03-11 | 2026-03-14 | 0 | 0 | shutdown 36 hr. | 10 | PASSED |  | WP-26-0033 | complete | pending
2026-03-09 | WFI08 | SV216.04 | Special | TRUE | 16-1-098 | Building 16 | CIP/SIP | WFI | 2026-03-11 | 2026-03-14 | 0 | 0 | shutdown 36 hr. | 10 | PASSED |  | WP-26-0033 | complete | pending
2026-03-09 | WFI09 | SV216.10 | Special | TRUE | 16-1-105 | Building 16 | WASHING/TUNNEL-01 | WFI | 2026-03-11 | 2026-03-14 | 0 | 0 | shutdown 36 hr. | 10 | PASSED |  | WP-26-0033 | complete | pending
2026-03-09 | WFI10 | POU HE216.04 | Special | TRUE | 16-1-114 | Building 16 | COMPOUNDING-02 | WFI | 2026-03-11 | 2026-03-14 | 0 | 0 | shutdown 36 hr. | 10 | PASSED |  | WP-26-0033 | complete | pending
2026-03-09 | WFI11 | POU HE216.05 | Special | TRUE | 16-1-114 | Building 16 | COMPOUNDING-02 | WFI | 2026-03-11 | 2026-03-14 | 0 | 0 | shutdown 36 hr. | 10 | PASSED |  | WP-26-0033 | complete | pending
2026-03-10 | GWFI03 | SV217.01 | Special | TRUE | 16-2-010 | Building 16 | RETURN LOOP | WFI | 2026-03-11 | 2026-03-14 | 0 | 0 |  | 10 | PASSED |  | WP-26-0034 | complete | pending
2026-03-16 | GWFI01 | V12-4 | PQ3-Day3 | TRUE | 16-2-010 | Building 16 | AFTER WFI GENERATOR | WFI | 2026-03-17 | 2026-03-21 | 0 | 0 |  | 10 | PASSED | FALSE | WP-26-0035 | complete | pending
2026-03-16 | GWFI02 | SV213.01 | PQ3-Day3 | TRUE | 16-2-010 | Building 16 | AFTER STORAGE TANK | WFI | 2026-03-17 | 2026-03-21 | 0 | 0 |  | 10 | PASSED | FALSE | WP-26-0035 | complete | pending
2026-03-16 | GWFI03 | SV217.01 | PQ3-Day3 | TRUE | 16-2-010 | Building 16 | RETURN LOOP | WFI | 2026-03-17 | 2026-03-21 | 0 | 0 |  | 10 | PASSED | FALSE | WP-26-0035 | complete | pending
2026-03-16 | WFI07 | SV216.02 | PQ3-Day3 | TRUE | 16-1-098 | Building 16 | CIP/SIP | WFI | 2026-03-17 | 2026-03-21 | 0 | 0 |  | 10 | PASSED | FALSE | WP-26-0035 | complete | pending
2026-03-16 | WFI08 | SV216.04 | PQ3-Day3 | TRUE | 16-1-098 | Building 16 | CIP/SIP | WFI | 2026-03-17 | 2026-03-21 | 0 | 0 |  | 10 | PASSED | FALSE | WP-26-0035 | complete | pending
2026-03-17 | WFI03 | SV216.03 | PQ3-Day3 | TRUE | 16-1-096 | Building 16 | WASHING/TUNNEL-02 | WFI | 2026-03-19 | 2026-03-24 | 0 | 0 |  | 10 | PASSED | FALSE | WP-26-0036 | complete | pending
2026-03-17 | WFI04 | POU HE216.03 | PQ3-Day3 | TRUE | 16-1-082 | Building 16 | WASHING | WFI | 2026-03-19 | 2026-03-24 | 0 | 0 |  | 10 | PASSED | FALSE | WP-26-0036 | complete | pending
2026-03-17 | WFI05 | SV216.06 | PQ3-Day3 | TRUE | 16-1-082 | Building 16 | WASHING | WFI | 2026-03-19 | 2026-03-24 | 0 | 0 |  | 10 | PASSED | FALSE | WP-26-0036 | complete | pending
2026-03-18 | WFI06 | SV216.05 | PQ3-Day3 | TRUE | 16-1-110 | Building 16 | DISINFECTANT PREPARATION | WFI | 2026-03-19 | 2026-03-24 | 0 | 0 |  | 10 | PASSED | FALSE | WP-26-0037 | complete | pending
2026-03-18 | WFI09 | SV216.10 | PQ3-Day3 | TRUE | 16-1-105 | Building 16 | WASHING/TUNNEL-01 | WFI | 2026-03-19 | 2026-03-24 | 0 | 0 |  | 10 | PASSED | FALSE | WP-26-0037 | complete | pending
2026-03-19 | WFI01 | POU HE216.01 | PQ3-Day3 | TRUE | 16-1-107 | Building 16 | COMPOUNDING-01 | WFI | 2026-03-21 | 2026-03-24 | 0 | 0 |  | 10 | PASSED | FALSE | WP-26-0038 | complete | pending
2026-03-19 | WFI02 | POU HE216.02 | PQ3-Day3 | TRUE | 16-1-107 | Building 16 | COMPOUNDING-01 | WFI | 2026-03-21 | 2026-03-24 | 0 | 0 |  | 10 | PASSED | FALSE | WP-26-0038 | complete | pending
2026-03-20 | WFI10 | POU HE216.04 | PQ3-Day3 | TRUE | 16-1-114 | Building 16 | COMPOUNDING-02 | WFI | 2026-03-21 | 2026-03-24 | 0 | 0 |  | 10 | PASSED | FALSE | WP-26-0039 | complete | pending
2026-03-20 | WFI11 | POU HE216.05 | PQ3-Day3 | TRUE | 16-1-114 | Building 16 | COMPOUNDING-02 | WFI | 2026-03-21 | 2026-03-24 | 0 | 0 |  | 10 | PASSED | FALSE | WP-26-0039 | complete | pending
2026-03-23 | GWFI01 | V12-4 | PQ3-Day4 | TRUE | 16-2-010 | Building 16 | AFTER WFI GENERATOR | WFI | 2026-03-24 | 2026-03-27 | 0 | 0 |  | 10 | PASSED | FALSE | WP-26-0040 | complete | pending
2026-03-23 | GWFI02 | SV213.01 | PQ3-Day4 | TRUE | 16-2-010 | Building 16 | AFTER STORAGE TANK | WFI | 2026-03-24 | 2026-03-27 | 0 | 0 |  | 10 | PASSED | FALSE | WP-26-0040 | complete | pending
2026-03-23 | GWFI03 | SV217.01 | PQ3-Day4 | TRUE | 16-2-010 | Building 16 | RETURN LOOP | WFI | 2026-03-24 | 2026-03-27 | 0 | 0 |  | 10 | PASSED | FALSE | WP-26-0040 | complete | pending
2026-03-23 | WFI07 | SV216.02 | PQ3-Day4 | TRUE | 16-1-098 | Building 16 | CIP/SIP | WFI | 2026-03-24 | 2026-03-27 | 0 | 0 |  | 10 | PASSED | TRUE | WP-26-0040 | complete | pending
2026-03-23 | WFI08 | SV216.04 | PQ3-Day4 | TRUE | 16-1-098 | Building 16 | CIP/SIP | WFI | 2026-03-24 | 2026-03-27 | 0 | 0 |  | 10 | PASSED | FALSE | WP-26-0040 | complete | pending
2026-03-24 | WFI03 | SV216.03 | PQ3-Day4 | TRUE | 16-1-096 | Building 16 | WASHING/TUNNEL-02 | WFI | 2026-03-26 | 2026-03-29 | 0 | 0 |  | 10 | PASSED | FALSE | WP-26-0041 | complete | pending
2026-03-24 | WFI04 | POU HE216.03 | PQ3-Day4 | TRUE | 16-1-082 | Building 16 | WASHING | WFI | 2026-03-26 | 2026-03-29 | 0 | 0 |  | 10 | PASSED | FALSE | WP-26-0041 | complete | pending
2026-03-24 | WFI05 | SV216.06 | PQ3-Day4 | TRUE | 16-1-082 | Building 16 | WASHING | WFI | 2026-03-26 | 2026-03-29 | 0 | 0 |  | 10 | PASSED | FALSE | WP-26-0041 | complete | pending
2026-03-25 | WFI10 | POU HE216.04 | PQ3-Day4 | TRUE | 16-1-114 | Building 16 | COMPOUNDING-02 | WFI | 2026-03-26 | 2026-03-29 | 0 | 0 |  | 10 | PASSED | FALSE | WP-26-0042 | complete | pending
2026-03-25 | WFI11 | POU HE216.05 | PQ3-Day4 | TRUE | 16-1-114 | Building 16 | COMPOUNDING-02 | WFI | 2026-03-26 | 2026-03-29 | 0 | 0 |  | 10 | PASSED | FALSE | WP-26-0042 | complete | pending
2026-03-26 | WFI01 | POU HE216.01 | PQ3-Day4 | TRUE | 16-1-107 | Building 16 | COMPOUNDING-01 | WFI | 2026-03-28 | 2026-03-31 | 0 | 0 |  | 10 | PASSED | FALSE | WP-26-0043 | complete | pending
2026-03-26 | WFI02 | POU HE216.02 | PQ3-Day4 | TRUE | 16-1-107 | Building 16 | COMPOUNDING-01 | WFI | 2026-03-28 | 2026-03-31 | 0 | 0 |  | 10 | PASSED | FALSE | WP-26-0043 | complete | pending
2026-03-27 | WFI06 | SV216.05 | PQ3-Day4 | TRUE | 16-1-110 | Building 16 | DISINFECTANT PREPARATION | WFI | 2026-03-28 | 2026-03-31 | 0 | 0 |  | 10 | PASSED | FALSE | WP-26-0044 | complete | pending
2026-03-27 | WFI09 | SV216.10 | PQ3-Day4 | TRUE | 16-1-105 | Building 16 | WASHING/TUNNEL-01 | WFI | 2026-03-28 | 2026-03-31 | 0 | 0 |  | 10 | PASSED | FALSE | WP-26-0044 | complete | pending
2026-03-30 | WFI10 | POU HE216.04 | PQ3-Day1 | TRUE | 16-1-114 | Building 16 | COMPOUNDING-02 | WFI | 2026-03-31 | 2026-04-03 | 0 | 0 |  | 10 | PASSED | FALSE | WP-26-0047 | complete | pending
2026-03-30 | WFI11 | POU HE216.05 | PQ3-Day1 | TRUE | 16-1-114 | Building 16 | COMPOUNDING-02 | WFI | 2026-03-31 | 2026-04-03 | 0 | 0 |  | 10 | PASSED | FALSE | WP-26-0047 | complete | pending
2026-03-30 | GWFI01 | V12-4 | PQ3-Day1 | TRUE | 16-2-010 | Building 16 | AFTER WFI GENERATOR | WFI | 2026-03-31 | 2026-04-03 | 0 | 0 |  | 10 | PASSED | FALSE | WP-26-0047 | complete | pending
2026-03-30 | GWFI02 | SV213.01 | PQ3-Day1 | TRUE | 16-2-010 | Building 16 | AFTER STORAGE TANK | WFI | 2026-03-31 | 2026-04-03 | 0 | 0 |  | 10 | PASSED | FALSE | WP-26-0047 | complete | pending
2026-03-30 | GWFI03 | SV217.01 | PQ3-Day1 | TRUE | 16-2-010 | Building 16 | RETURN LOOP | WFI | 2026-03-31 | 2026-04-03 | 0 | 0 |  | 10 | PASSED | FALSE | WP-26-0047 | complete | pending
2026-03-30 | WFI03 | SV216.03 | PQ3-Day1 | TRUE | 16-1-096 | Building 16 | WASHING/TUNNEL-02 | WFI | 2026-03-31 | 2026-04-03 | 0 | 0 |  | 10 | PASSED | FALSE | WP-26-0047 | complete | pending
2026-03-31 | WFI04 | POU HE216.03 | PQ3-Day2 | TRUE | 16-1-082 | Building 16 | WASHING | WFI | 2026-04-02 | 2026-04-08 | 0 | 0 |  | 10 | PASSED | FALSE | WP-26-0049 | complete | pending
2026-03-31 | WFI05 | SV216.06 | PQ3-Day2 | TRUE | 16-1-082 | Building 16 | WASHING | WFI | 2026-04-02 | 2026-04-08 | 0 | 0 |  | 10 | PASSED | FALSE | WP-26-0049 | complete | pending
2026-04-01 | WFI07 | SV216.02 | PQ3-Day3 | TRUE | 16-1-098 | Building 16 | CIP/SIP | WFI | 2026-04-03 | 2026-04-08 | 0 | 0 |  | 10 | PASSED | FALSE | WP-26-0048 | complete | pending
2026-04-01 | WFI08 | SV216.04 | PQ3-Day3 | TRUE | 16-1-098 | Building 16 | CIP/SIP | WFI | 2026-04-03 | 2026-04-08 | 0 | 0 |  | 10 | PASSED | FALSE | WP-26-0048 | complete | pending
2026-04-02 | WFI06 | SV216.05 | PQ3-Day4 | TRUE | 16-1-110 | Building 16 | DISINFECTANT PREPARATION | WFI | 2026-04-03 | 2026-04-08 | 0 | 0 |  | 10 | PASSED | FALSE | WP-26-0050 | complete | pending
2026-04-02 | WFI09 | SV216.10 | PQ3-Day4 | TRUE | 16-1-105 | Building 16 | WASHING/TUNNEL-01 | WFI | 2026-04-03 | 2026-04-08 | 0 | 0 |  | 10 | PASSED | FALSE | WP-26-0050 | complete | pending
2026-04-03 | WFI01 | POU HE216.01 | PQ3-Day5 | TRUE | 16-1-107 | Building 16 | COMPOUNDING-01 | WFI | 2026-04-04 | 2026-04-08 | 0 | 0 |  | 10 | PASSED | FALSE | WP-26-0051 | complete | pending
2026-04-03 | WFI02 | POU HE216.02 | PQ3-Day5 | TRUE | 16-1-107 | Building 16 | COMPOUNDING-01 | WFI | 2026-04-04 | 2026-04-08 | 0 | 0 |  | 10 | PASSED | FALSE | WP-26-0051 | complete | pending
2026-04-07 | GWFI01 | V12-4 | PQ3-Day1 | TRUE | 16-2-010 | Building 16 | AFTER WFI GENERATOR | WFI | 2026-04-09 | 2026-04-15 | 0 | 0 |  | 10 | PASSED | FALSE | WP-26-0052 | complete | pending
2026-04-07 | GWFI02 | SV213.01 | PQ3-Day1 | TRUE | 16-2-010 | Building 16 | AFTER STORAGE TANK | WFI | 2026-04-09 | 2026-04-15 | 0 | 0 |  | 10 | PASSED | FALSE | WP-26-0052 | complete | pending
2026-04-07 | GWFI03 | SV217.01 | PQ3-Day1 | TRUE | 16-2-010 | Building 16 | RETURN LOOP | WFI | 2026-04-09 | 2026-04-15 | 0 | 0 |  | 10 | PASSED | FALSE | WP-26-0052 | complete | pending
2026-04-07 | WFI03 | SV216.03 | PQ3-Day1 | TRUE | 16-1-096 | Building 16 | WASHING/TUNNEL-02 | WFI | 2026-04-09 | 2026-04-15 | 0 | 0 |  | 10 | PASSED | FALSE | WP-26-0052 | complete | pending
2026-04-07 | WFI04 | POU HE216.03 | PQ3-Day1 | TRUE | 16-1-082 | Building 16 | WASHING | WFI | 2026-04-09 | 2026-04-15 | 0 | 0 |  | 10 | PASSED | FALSE | WP-26-0052 | complete | pending
2026-04-07 | WFI05 | SV216.06 | PQ3-Day1 | TRUE | 16-1-082 | Building 16 | WASHING | WFI | 2026-04-09 | 2026-04-15 | 0 | 0 |  | 10 | PASSED | FALSE | WP-26-0052 | complete | pending
2026-04-07 | WFI07 | SV216.02 | PQ3-Day1 | TRUE | 16-1-098 | Building 16 | CIP/SIP | WFI | 2026-04-09 | 2026-04-15 | 0 | 0 |  | 10 | PASSED | FALSE | WP-26-0052 | complete | pending
2026-04-08 | WFI06 | SV216.05 | PQ3-Day2 | TRUE | 16-1-110 | Building 16 | DISINFECTANT PREPARATION | WFI | 2026-04-09 | 2026-04-15 | 0 | 0 |  | 10 | PASSED | FALSE | WP-26-0053 | complete | pending
2026-04-08 | WFI09 | SV216.10 | PQ3-Day2 | TRUE | 16-1-105 | Building 16 | WASHING/TUNNEL-01 | WFI | 2026-04-09 | 2026-04-15 | 0 | 0 |  | 10 | PASSED | FALSE | WP-26-0053 | complete | pending
2026-04-09 | WFI01 | POU HE216.01 | PQ3-Day3 | TRUE | 16-1-107 | Building 16 | COMPOUNDING-01 | WFI | 2026-04-11 | 2026-04-15 | 0 | 0 |  | 10 | PASSED | FALSE | WP-26-0054 | complete | pending
2026-04-09 | WFI02 | POU HE216.02 | PQ3-Day3 | TRUE | 16-1-107 | Building 16 | COMPOUNDING-01 | WFI | 2026-04-11 | 2026-04-15 | 0 | 0 |  | 10 | PASSED | FALSE | WP-26-0054 | complete | pending
2026-04-10 | WFI08 | SV216.04 | PQ3-Day4 | TRUE | 16-1-098 | Building 16 | CIP/SIP | WFI | 2026-04-11 | 2026-04-15 | 0 | 0 |  | 10 | PASSED | FALSE | WP-26-0055 | complete | pending
2026-04-10 | WFI10 | POU HE216.04 | PQ3-Day4 | TRUE | 16-1-114 | Building 16 | COMPOUNDING-02 | WFI | 2026-04-11 | 2026-04-15 | 0 | 0 |  | 10 | PASSED | FALSE | WP-26-0055 | complete | pending
2026-04-10 | WFI11 | POU HE216.05 | PQ3-Day4 | TRUE | 16-1-114 | Building 16 | COMPOUNDING-02 | WFI | 2026-04-11 | 2026-04-15 | 1 | 1 |  | 10 | PASSED | FALSE | WP-26-0055 | complete | pending
2026-04-20 | GWFI01 | V12-4 | PQ3-Day1 | TRUE | 16-2-010 | Building 16 | AFTER WFI GENERATOR | WFI | 2026-04-22 | 2026-04-25 | 0 | 0 |  | 10 | PASSED | FALSE | WP-26-0056 | complete | pending
2026-04-20 | GWFI02 | SV213.01 | PQ3-Day1 | TRUE | 16-2-010 | Building 16 | AFTER STORAGE TANK | WFI | 2026-04-22 | 2026-04-25 | 0 | 0 |  | 10 | PASSED | FALSE | WP-26-0056 | complete | pending
2026-04-20 | GWFI03 | SV217.01 | PQ3-Day1 | TRUE | 16-2-010 | Building 16 | RETURN LOOP | WFI | 2026-04-22 | 2026-04-25 | 0 | 0 |  | 10 | PASSED | FALSE | WP-26-0056 | complete | pending
2026-04-20 | WFI07 | SV216.02 | PQ3-Day1 | TRUE | 16-1-098 | Building 16 | CIP/SIP | WFI | 2026-04-22 | 2026-04-25 | 0 | 0 |  | 10 | PASSED | FALSE | WP-26-0056 | complete | pending
2026-04-20 | WFI08 | SV216.04 | PQ3-Day1 | TRUE | 16-1-098 | Building 16 | CIP/SIP | WFI | 2026-04-22 | 2026-04-25 | 0 | 0 |  | 10 | PASSED | FALSE | WP-26-0056 | complete | pending
2026-04-21 | WFI03 | SV216.03 | PQ3-Day2 | TRUE | 16-1-096 | Building 16 | WASHING/TUNNEL-02 | WFI | 2026-04-22 | 2026-04-25 | 0 | 0 |  | 10 | PASSED | FALSE | WP-26-0057 | complete | pending
2026-04-21 | WFI04 | POU HE216.03 | PQ3-Day2 | TRUE | 16-1-082 | Building 16 | WASHING | WFI | 2026-04-22 | 2026-04-25 | 0 | 0 |  | 10 | PASSED | FALSE | WP-26-0057 | complete | pending
2026-04-21 | WFI05 | SV216.06 | PQ3-Day2 | TRUE | 16-1-082 | Building 16 | WASHING | WFI | 2026-04-22 | 2026-04-25 | 0 | 0 |  | 10 | PASSED | FALSE | WP-26-0057 | complete | pending
2026-04-22 | WFI06 | SV216.05 | PQ3-Day3 | TRUE | 16-1-110 | Building 16 | DISINFECTANT PREPARATION | WFI | 2026-04-24 | 2026-04-27 | 0 | 0 |  | 10 | PASSED | FALSE | WP-26-0058 | complete | pending
2026-04-22 | WFI09 | SV216.10 | PQ3-Day3 | TRUE | 16-1-105 | Building 16 | WASHING/TUNNEL-01 | WFI | 2026-04-24 | 2026-04-27 | 0 | 0 |  | 10 | PASSED | FALSE | WP-26-0058 | complete | pending
2026-04-23 | WFI01 | POU HE216.01 | PQ3-Day4 | TRUE | 16-1-107 | Building 16 | COMPOUNDING-01 | WFI | 2026-04-24 | 2026-04-27 | 0 | 0 |  | 10 | PASSED | FALSE | WP-26-0059 | complete | pending
2026-04-23 | WFI02 | POU HE216.02 | PQ3-Day4 | TRUE | 16-1-107 | Building 16 | COMPOUNDING-01 | WFI | 2026-04-24 | 2026-04-27 | 1 | 1 |  | 10 | PASSED | FALSE | WP-26-0059 | complete | pending
2026-04-24 | WFI10 | POU HE216.04 | PQ3-Day5 | TRUE | 16-1-114 | Building 16 | COMPOUNDING-02 | WFI | 2026-04-25 | 2026-04-29 | 0 | 0 |  | 10 | PASSED | FALSE | WT-26-0083 | complete | synced
2026-04-24 | WFI11 | POU HE216.05 | PQ3-Day5 | TRUE | 16-1-114 | Building 16 | COMPOUNDING-02 | WFI | 2026-04-25 | 2026-04-29 | 0 | 0 |  | 10 | PASSED | FALSE | WT-26-0083 | complete | synced
2026-04-27 | GWFI01 | V12-4 | PQ3-Day1 | TRUE | 16-2-010 | Building 16 | AFTER WFI GENERATOR | WFI | 2026-04-29 | 2026-05-06 | 0 | 0 |  | 10 | PASSED | FALSE | WT-26-0084 | complete | synced
2026-04-27 | GWFI02 | SV213.01 | PQ3-Day1 | TRUE | 16-2-010 | Building 16 | AFTER STORAGE TANK | WFI | 2026-04-29 | 2026-05-06 | 0 | 0 |  | 10 | PASSED | FALSE | WT-26-0084 | complete | synced
2026-04-27 | GWFI03 | SV217.01 | PQ3-Day1 | TRUE | 16-2-010 | Building 16 | RETURN LOOP | WFI | 2026-04-29 | 2026-05-06 | 0 | 0 |  | 10 | PASSED | FALSE | WT-26-0084 | complete | synced
2026-04-27 | WFI03 | SV216.03 | PQ3-Day2 | TRUE | 16-1-096 | Building 16 | WASHING/TUNNEL-02 | WFI | 2026-04-29 | 2026-05-06 | 0 | 0 |  | 10 | PASSED | FALSE | WT-26-0084 | complete | synced
2026-04-27 | WFI04 | POU HE216.03 | PQ3-Day2 | TRUE | 16-1-082 | Building 16 | WASHING | WFI | 2026-04-29 | 2026-05-06 | 0 | 0 |  | 10 | PASSED | FALSE | WT-26-0084 | complete | synced
2026-04-27 | WFI05 | SV216.06 | PQ3-Day2 | TRUE | 16-1-082 | Building 16 | WASHING | WFI | 2026-04-29 | 2026-05-06 | 0 | 0 |  | 10 | PASSED | FALSE | WT-26-0084 | complete | synced
2026-04-27 | WFI07 | SV216.02 | PQ3-Day2 | TRUE | 16-1-098 | Building 16 | CIP/SIP | WFI | 2026-04-29 | 2026-05-06 | 0 | 0 |  | 10 | PASSED | FALSE | WT-26-0084 | complete | synced
2026-04-28 | WFI06 | SV216.05 | PQ3-Day3 | TRUE | 16-1-110 | Building 16 | DISINFECTANT PREPARATION | WFI | 2026-04-29 | 2026-05-06 | 0 | 0 |  | 10 | PASSED | FALSE | WP-26-0061 | complete | pending
2026-04-28 | WFI09 | SV216.10 | PQ3-Day3 | TRUE | 16-1-105 | Building 16 | WASHING/TUNNEL-01 | WFI | 2026-04-29 | 2026-05-06 | 0 | 0 |  | 10 | PASSED | FALSE | WP-26-0061 | complete | pending
2026-04-29 | WFI01 | POU HE216.01 | PQ3-Day4 | TRUE | 16-1-107 | Building 16 | COMPOUNDING-01 | WFI | 2026-05-01 | 2026-05-06 | 0 | 0 |  | 10 | PASSED | FALSE | WP-26-0062 | complete | pending
2026-04-29 | WFI02 | POU HE216.02 | PQ3-Day4 | TRUE | 16-1-107 | Building 16 | COMPOUNDING-01 | WFI | 2026-05-01 | 2026-05-06 | 0 | 0 |  | 10 | PASSED | FALSE | WP-26-0062 | complete | pending
2026-04-30 | WFI08 | SV216.04 | PQ3-Day5 | TRUE | 16-1-098 | Building 16 | CIP/SIP | WFI | 2026-05-01 | 2026-05-06 | 0 | 0 |  | 10 | PASSED | FALSE | WP-26-0063 | complete | pending
2026-04-30 | WFI10 | POU HE216.04 | PQ3-Day5 | TRUE | 16-1-114 | Building 16 | COMPOUNDING-02 | WFI | 2026-05-01 | 2026-05-06 | 0 | 0 |  | 10 | PASSED | FALSE | WP-26-0063 | complete | pending
2026-04-30 | WFI11 | POU HE216.05 | PQ3-Day5 | TRUE | 16-1-114 | Building 16 | COMPOUNDING-02 | WFI | 2026-05-01 | 2026-05-06 | 0 | 0 |  | 10 | PASSED | FALSE | WP-26-0063 | complete | pending
2026-05-05 | GWFI01 | V12-4 | PQ3-Day1 | TRUE | 16-2-010 | Building 16 | AFTER WFI GENERATOR | WFI | 2026-05-07 | 2026-05-12 | 0 | 0 |  | 10 | PASSED | FALSE | WP-26-0064 | complete | pending
2026-05-05 | GWFI02 | SV213.01 | PQ3-Day1 | TRUE | 16-2-010 | Building 16 | AFTER STORAGE TANK | WFI | 2026-05-07 | 2026-05-12 | 0 | 0 |  | 10 | PASSED | FALSE | WP-26-0064 | complete | pending
2026-05-05 | GWFI03 | SV217.01 | PQ3-Day1 | TRUE | 16-2-010 | Building 16 | RETURN LOOP | WFI | 2026-05-07 | 2026-05-12 | 0 | 0 |  | 10 | PASSED | FALSE | WP-26-0064 | complete | pending
2026-05-05 | WFI07 | SV216.02 | PQ3-Day1 | TRUE | 16-1-098 | Building 16 | CIP/SIP | WFI | 2026-05-07 | 2026-05-12 | 0 | 0 |  | 10 | PASSED | FALSE | WP-26-0064 | complete | pending
2026-05-05 | WFI08 | SV216.04 | PQ3-Day1 | TRUE | 16-1-098 | Building 16 | CIP/SIP | WFI | 2026-05-07 | 2026-05-12 | 0 | 0 |  | 10 | PASSED | FALSE | WP-26-0064 | complete | pending
2026-05-06 | WFI01 | POU HE216.01 | PQ3-Day2 | TRUE | 16-1-107 | Building 16 | COMPOUNDING-01 | WFI | 2026-05-07 | 2026-05-12 | 0 | 0 |  | 10 | PASSED | FALSE | WP-26-0065 | complete | pending
2026-05-06 | WFI02 | POU HE216.02 | PQ3-Day2 | TRUE | 16-1-107 | Building 16 | COMPOUNDING-01 | WFI | 2026-05-07 | 2026-05-12 | 0 | 0 |  | 10 | PASSED | FALSE | WP-26-0065 | complete | pending
2026-05-07 | WFI06 | SV216.05 | PQ3-Day3 | TRUE | 16-1-110 | Building 16 | DISINFECTANT PREPARATION | WFI | 2026-05-09 | 2026-05-12 | 0 | 0 |  | 10 | PASSED | FALSE | WP-26-0066 | complete | pending
2026-05-07 | WFI09 | SV216.10 | PQ3-Day3 | TRUE | 16-1-105 | Building 16 | WASHING/TUNNEL-01 | WFI | 2026-05-09 | 2026-05-12 | 0 | 0 |  | 10 | PASSED | FALSE | WP-26-0066 | complete | pending
2026-05-07 | WFI10 | POU HE216.04 | PQ3-Day3 | TRUE | 16-1-114 | Building 16 | COMPOUNDING-02 | WFI | 2026-05-09 | 2026-05-12 | 59 | 59 |  | 10 | NOT-PASSED | FALSE | WP-26-0066 | complete | pending
2026-05-07 | WFI11 | POU HE216.05 | PQ3-Day3 | TRUE | 16-1-114 | Building 16 | COMPOUNDING-02 | WFI | 2026-05-09 | 2026-05-12 | 2 | 2 |  | 10 | PASSED | FALSE | WP-26-0066 | complete | pending
2026-05-08 | WFI03 | SV216.03 | PQ3-Day4 | TRUE | 16-1-096 | Building 16 | WASHING/TUNNEL-02 | WFI | 2026-05-09 | 2026-05-12 | 0 | 0 |  | 10 | PASSED | FALSE | WP-26-0067 | complete | pending
2026-05-08 | WFI04 | POU HE216.03 | PQ3-Day4 | TRUE | 16-1-082 | Building 16 | WASHING | WFI | 2026-05-09 | 2026-05-12 | 0 | 0 |  | 10 | PASSED | FALSE | WP-26-0067 | complete | pending
2026-05-08 | WFI05 | SV216.06 | PQ3-Day4 | TRUE | 16-1-082 | Building 16 | WASHING | WFI | 2026-05-09 | 2026-05-12 | 0 | 0 |  | 10 | PASSED | FALSE | WP-26-0067 | complete | pending
2026-05-11 | GWFI01 | V12-4 | PQ3-Day1 | TRUE | 16-2-010 | Building 16 | AFTER WFI GENERATOR | WFI | 2026-05-13 | 2026-05-16 | 0 | 0 |  | 10 | PASSED | FALSE | WP-26-0068 | complete | pending
2026-05-11 | GWFI02 | SV213.01 | PQ3-Day1 | TRUE | 16-2-010 | Building 16 | AFTER STORAGE TANK | WFI | 2026-05-13 | 2026-05-16 | 0 | 0 |  | 10 | PASSED | FALSE | WP-26-0068 | complete | pending
2026-05-11 | GWFI03 | SV217.01 | PQ3-Day1 | TRUE | 16-2-010 | Building 16 | RETURN LOOP | WFI | 2026-05-13 | 2026-05-16 | 0 | 0 |  | 10 | PASSED | FALSE | WP-26-0068 | complete | pending
2026-05-11 | WFI07 | SV216.02 | PQ3-Day1 | TRUE | 16-1-098 | Building 16 | CIP/SIP | WFI | 2026-05-13 | 2026-05-16 | 0 | 0 |  | 10 | PASSED | FALSE | WP-26-0068 | complete | pending
2026-05-11 | WFI08 | SV216.04 | PQ3-Day1 | TRUE | 16-1-098 | Building 16 | CIP/SIP | WFI | 2026-05-13 | 2026-05-16 | 0 | 0 |  | 10 | PASSED | FALSE | WP-26-0068 | complete | pending
2026-05-12 | WFI01 | POU HE216.01 | PQ3-Day2 | TRUE | 16-1-107 | Building 16 | COMPOUNDING-01 | WFI | 2026-05-13 | 2026-05-16 | 0 | 0 |  | 10 | PASSED | FALSE | WP-26-0069 | complete | pending
2026-05-12 | WFI02 | POU HE216.02 | PQ3-Day2 | TRUE | 16-1-107 | Building 16 | COMPOUNDING-01 | WFI | 2026-05-13 | 2026-05-16 | 0 | 0 |  | 10 | PASSED | FALSE | WP-26-0069 | complete | pending
2026-05-14 | WFI06 | SV216.05 | PQ3-Day3 | TRUE | 16-1-110 | Building 16 | DISINFECTANT PREPARATION | WFI | 2026-05-16 | 2026-05-19 | 0 | 0 |  | 10 | PASSED | FALSE | WP-26-0070 | complete | pending
2026-05-14 | WFI09 | SV216.10 | PQ3-Day3 | TRUE | 16-1-105 | Building 16 | WASHING/TUNNEL-01 | WFI | 2026-05-16 | 2026-05-19 | 0 | 0 |  | 10 | PASSED | FALSE | WP-26-0070 | complete | pending
2026-05-15 | WFI03 | SV216.03 | PQ3-Day4 | TRUE | 16-1-096 | Building 16 | WASHING/TUNNEL-02 | WFI | 2026-05-16 | 2026-05-19 | 0 | 0 |  | 10 | PASSED | FALSE | WP-26-0071 | complete | pending
2026-05-15 | WFI04 | POU HE216.03 | PQ3-Day4 | TRUE | 16-1-082 | Building 16 | WASHING | WFI | 2026-05-16 | 2026-05-19 | 0 | 0 |  | 10 | PASSED | FALSE | WP-26-0071 | complete | pending
2026-05-15 | WFI05 | SV216.06 | PQ3-Day4 | TRUE | 16-1-082 | Building 16 | WASHING | WFI | 2026-05-16 | 2026-05-19 | 0 | 0 |  | 10 | PASSED | FALSE | WP-26-0071 | complete | pending
2026-05-15 | WFI10 | POU HE216.04 | PQ3-Day4 | TRUE | 16-1-114 | Building 16 | COMPOUNDING-02 | WFI | 2026-05-16 | 2026-05-19 | 0 | 0 |  | 10 | PASSED | FALSE | WP-26-0071 | complete | pending
2026-05-15 | WFI11 | POU HE216.05 | PQ3-Day4 | TRUE | 16-1-114 | Building 16 | COMPOUNDING-02 | WFI | 2026-05-16 | 2026-05-19 | 0 | 0 |  | 10 | PASSED | FALSE | WP-26-0071 | complete | pending
2026-05-18 | GWFI01 | V12-4 | PQ3-Day1 | TRUE | 16-2-010 | Building 16 | AFTER WFI GENERATOR | WFI | 2026-05-19 | 2026-05-23 | 0 | 0 |  |  | PASSED | FALSE | WP-26-0072 | complete | pending
2026-05-18 | GWFI02 | SV213.01 | PQ3-Day1 | TRUE | 16-2-010 | Building 16 | AFTER STORAGE TANK | WFI | 2026-05-19 | 2026-05-23 | 0 | 0 |  |  | PASSED | FALSE | WP-26-0072 | complete | pending
2026-05-18 | GWFI03 | SV217.01 | PQ3-Day1 | TRUE | 16-2-010 | Building 16 | RETURN LOOP | WFI | 2026-05-19 | 2026-05-23 | 0 | 0 |  |  | PASSED | FALSE | WP-26-0072 | complete | pending
2026-05-18 | WFI07 | SV216.02 | PQ3-Day1 | TRUE | 16-1-098 | Building 16 | CIP/SIP | WFI | 2026-05-19 | 2026-05-23 | 0 | 0 |  |  | PASSED | FALSE | WP-26-0072 | complete | pending
2026-05-18 | WFI08 | SV216.04 | PQ3-Day1 | TRUE | 16-1-098 | Building 16 | CIP/SIP | WFI | 2026-05-19 | 2026-05-23 | 0 | 0 |  |  | PASSED | FALSE | WP-26-0072 | complete | pending
2026-05-19 | WFI03 | SV216.03 | PQ3-Day2 | TRUE | 16-1-096 | Building 16 | WASHING/TUNNEL-02 | WFI | 2026-05-21 | 2026-05-25 | 0 | 0 |  |  | PASSED | FALSE | WP-26-0073 | complete | pending
2026-05-19 | WFI04 | POU HE216.03 | PQ3-Day2 | TRUE | 16-1-082 | Building 16 | WASHING | WFI | 2026-05-21 | 2026-05-25 | 0 | 0 |  |  | PASSED | FALSE | WP-26-0073 | complete | pending
2026-05-19 | WFI05 | SV216.06 | PQ3-Day3 | TRUE | 16-1-082 | Building 16 | WASHING | WFI | 2026-05-21 | 2026-05-25 | 0 | 0 |  |  | PASSED | FALSE | WP-26-0073 | complete | pending
2026-05-20 | WFI01 | POU HE216.01 | PQ3-Day3 | TRUE | 16-1-107 | Building 16 | COMPOUNDING-01 | WFI | 2026-05-22 | 2026-05-25 | 0 | 0 |  |  | PASSED | FALSE | WP-26-0074 | complete | pending
2026-05-20 | WFI02 | POU HE216.02 | PQ3-Day3 | TRUE | 16-1-107 | Building 16 | COMPOUNDING-01 | WFI | 2026-05-22 | 2026-05-25 | 0 | 0 |  |  | PASSED | FALSE | WP-26-0074 | complete | pending
2026-05-21 | WFI06 | SV216.05 | PQ3-Day4 | TRUE | 16-1-110 | Building 16 | DISINFECTANT PREPARATION | WFI | 2026-05-23 | 2026-05-31 | 0 | 0 |  |  | PASSED | FALSE | WP-26-0075 | complete | pending
2026-05-21 | WFI09 | SV216.10 | PQ3-Day4 | TRUE | 16-1-105 | Building 16 | WASHING/TUNNEL-01 | WFI | 2026-05-23 | 2026-05-31 | 0 | 0 |  |  | PASSED | FALSE | WP-26-0075 | complete | pending
2026-05-22 | WFI10 | POU HE216.04 | PQ3-Day5 | TRUE | 16-1-114 | Building 16 | COMPOUNDING-02 | WFI | 2026-05-23 | 2026-05-31 | 0 | 0 |  |  | PASSED | FALSE | WP-26-0076 | complete | pending
2026-05-22 | WFI11 | POU HE216.05 | PQ3-Day5 | TRUE | 16-1-114 | Building 16 | COMPOUNDING-02 | WFI | 2026-05-23 | 2026-05-31 | 0 | 0 |  |  | PASSED | FALSE | WP-26-0076 | complete | pending
2026-05-25 | GWFI01 | V12-4 | PQ3-Day1 | TRUE | 16-2-010 | Building 16 | AFTER WFI GENERATOR | WFI | 2026-05-26 | 2026-05-29 | 0 | 0 |  |  | PASSED | FALSE | WP-26-0077 | complete | pending
2026-05-25 | GWFI02 | SV213.01 | PQ3-Day1 | TRUE | 16-2-010 | Building 16 | AFTER STORAGE TANK | WFI | 2026-05-26 | 2026-05-29 | 0 | 0 |  |  | PASSED | FALSE | WP-26-0077 | complete | pending
2026-05-25 | GWFI03 | SV217.01 | PQ3-Day1 | TRUE | 16-2-010 | Building 16 | RETURN LOOP | WFI | 2026-05-26 | 2026-05-29 | 0 | 0 |  |  | PASSED | FALSE | WP-26-0077 | complete | pending
2026-05-25 | WFI07 | SV216.02 | PQ3-Day1 | TRUE | 16-1-098 | Building 16 | CIP/SIP | WFI | 2026-05-26 | 2026-05-29 | 0 | 0 |  |  | PASSED | FALSE | WP-26-0077 | complete | pending
2026-05-25 | WFI08 | SV216.04 | PQ3-Day1 | TRUE | 16-1-098 | Building 16 | CIP/SIP | WFI | 2026-05-26 | 2026-05-29 | 0 | 0 |  |  | PASSED | FALSE | WP-26-0077 | complete | pending
2026-05-26 | WFI03 | SV216.03 | PQ3-Day2 | TRUE | 16-1-096 | Building 16 | WASHING/TUNNEL-02 | WFI | 2026-05-28 | 2026-05-31 | 0 | 0 |  |  | PASSED | FALSE | WP-26-0078 | complete | pending
2026-05-26 | WFI04 | POU HE216.03 | PQ3-Day2 | TRUE | 16-1-082 | Building 16 | WASHING | WFI | 2026-05-28 | 2026-05-31 | 0 | 0 |  |  | PASSED | FALSE | WP-26-0078 | complete | pending
2026-05-26 | WFI05 | SV216.06 | PQ3-Day2 | TRUE | 16-1-082 | Building 16 | WASHING | WFI | 2026-05-28 | 2026-05-31 | 0 | 0 |  |  | PASSED | FALSE | WP-26-0078 | complete | pending
2026-05-27 | WFI01 | POU HE216.01 | PQ3-Day3 | TRUE | 16-1-107 | Building 16 | COMPOUNDING-01 | WFI | 2026-05-28 | 2026-05-31 | 0 | 0 |  |  | PASSED | FALSE | WP-26-0079 | complete | pending
2026-05-27 | WFI02 | POU HE216.02 | PQ3-Day3 | TRUE | 16-1-107 | Building 16 | COMPOUNDING-01 | WFI | 2026-05-28 | 2026-05-31 | 0 | 0 |  |  | PASSED | FALSE | WP-26-0079 | complete | pending
2026-05-28 | WFI06 | SV216.05 | PQ3-Day4 | TRUE | 16-1-110 | Building 16 | DISINFECTANT PREPARATION | WFI | 2026-05-30 | 2026-06-02 | 0 | 0 |  |  | PASSED | FALSE | WP-26-0080 | complete | pending
2026-05-28 | WFI09 | SV216.10 | PQ3-Day4 | TRUE | 16-1-105 | Building 16 | WASHING/TUNNEL-01 | WFI | 2026-05-30 | 2026-06-02 | 0 | 0 |  |  | PASSED | FALSE | WP-26-0080 | complete | pending
2026-05-29 | WFI10 | POU HE216.04 | PQ3-Day5 | TRUE | 16-1-114 | Building 16 | COMPOUNDING-02 | WFI | 2026-05-30 | 2026-06-02 | 0 | 0 |  |  | PASSED | FALSE | WP-26-0081 | complete | pending
2026-05-29 | WFI11 | POU HE216.05 | PQ3-Day5 | TRUE | 16-1-114 | Building 16 | COMPOUNDING-02 | WFI | 2026-05-30 | 2026-06-02 | 0 | 0 |  |  | PASSED | FALSE | WP-26-0081 | complete | pending
2026-06-02 | GWFI01 | V12-4 | PQ3-Day1 | TRUE | 16-2-010 | Building 16 | AFTER WFI GENERATOR | WFI | 2026-06-03 | 2026-06-06 | 0 | 0 |  |  | PASSED | FALSE | WP-26-0082 | complete | pending
2026-06-02 | GWFI02 | SV213.01 | PQ3-Day1 | TRUE | 16-2-010 | Building 16 | AFTER STORAGE TANK | WFI | 2026-06-03 | 2026-06-06 | 0 | 0 |  |  | PASSED | FALSE | WP-26-0082 | complete | pending
2026-06-02 | GWFI03 | SV217.01 | PQ3-Day1 | TRUE | 16-2-010 | Building 16 | RETURN LOOP | WFI | 2026-06-03 | 2026-06-06 | 0 | 0 |  |  | PASSED | FALSE | WP-26-0082 | complete | pending
2026-06-02 | WFI03 | SV216.03 | PQ3-Day1 | TRUE | 16-1-096 | Building 16 | WASHING/TUNNEL-02 | WFI | 2026-06-03 | 2026-06-06 | 0 | 0 |  |  | PASSED | FALSE | WP-26-0082 | complete | pending
2026-06-02 | WFI04 | POU HE216.03 | PQ3-Day1 | TRUE | 16-1-082 | Building 16 | WASHING | WFI | 2026-06-03 | 2026-06-06 | 0 | 0 |  |  | PASSED | FALSE | WP-26-0082 | complete | pending
2026-06-02 | WFI05 | SV216.06 | PQ3-Day1 | TRUE | 16-1-082 | Building 16 | WASHING | WFI | 2026-06-03 | 2026-06-06 | 0 | 0 |  |  | PASSED | FALSE | WP-26-0082 | complete | pending
2026-06-04 | WFI01 | POU HE216.01 | PQ3-Day2 | TRUE | 16-1-107 | Building 16 | COMPOUNDING-01 | WFI | 2026-06-05 | 2026-06-08 | 0 | 0 |  |  | PASSED | FALSE | WP-26-0083 | complete | pending
2026-06-04 | WFI02 | POU HE216.02 | PQ3-Day2 | TRUE | 16-1-107 | Building 16 | COMPOUNDING-01 | WFI | 2026-06-05 | 2026-06-08 | 0 | 0 |  |  | PASSED | FALSE | WP-26-0083 | complete | pending
2026-06-04 | WFI09 | SV216.10 | PQ3-Day2 | TRUE | 16-1-105 | Building 16 | WASHING/TUNNEL-01 | WFI | 2026-06-05 | 2026-06-08 | 0 | 0 |  |  | PASSED | FALSE | WP-26-0083 | complete | pending
2026-06-05 | WFI06 | SV216.05 | PQ3-Day3 | TRUE | 16-1-110 | Building 16 | DISINFECTANT PREPARATION | WFI | 2026-06-05 | 2026-06-08 | 0 | 0 |  |  | PASSED | FALSE | WP-26-0084 | complete | pending
2026-06-05 | WFI07 | SV216.02 | PQ3-Day3 | TRUE | 16-1-098 | Building 16 | CIP/SIP | WFI | 2026-06-05 | 2026-06-08 | 0 | 0 |  |  | PASSED | FALSE | WP-26-0084 | complete | pending
2026-06-05 | WFI08 | SV216.04 | PQ3-Day3 | TRUE | 16-1-098 | Building 16 | CIP/SIP | WFI | 2026-06-05 | 2026-06-08 | 0 | 0 |  |  | PASSED | FALSE | WP-26-0084 | complete | pending
2026-06-05 | WFI10 | POU HE216.04 | PQ3-Day3 | TRUE | 16-1-114 | Building 16 | COMPOUNDING-02 | WFI | 2026-06-05 | 2026-06-08 | 0 | 0 |  |  | PASSED | FALSE | WP-26-0084 | complete | pending
2026-06-05 | WFI11 | POU HE216.05 | PQ3-Day3 | TRUE | 16-1-114 | Building 16 | COMPOUNDING-02 | WFI | 2026-06-05 | 2026-06-08 | 0 | 0 |  |  | PASSED | FALSE | WP-26-0084 | complete | pending
2026-06-08 | GWFI01 | V12-4 | PQ3-Day1 | FALSE | 16-2-010 | Building 16 | AFTER WFI GENERATOR | WFI | 2026-06-09 | [5 empty] | PASSED | FALSE |  | pending
2026-06-08 | GWFI02 | SV213.01 | PQ3-Day1 | FALSE | 16-2-010 | Building 16 | AFTER STORAGE TANK | WFI | 2026-06-09 | [5 empty] | PASSED | FALSE |  | pending
2026-06-08 | GWFI03 | SV217.01 | PQ3-Day1 | FALSE | 16-2-010 | Building 16 | RETURN LOOP | WFI | 2026-06-09 | [5 empty] | PASSED | FALSE |  | pending
2026-06-08 | WFI07 | SV216.02 | PQ3-Day1 | FALSE | 16-1-098 | Building 16 | CIP/SIP | WFI | 2026-06-09 | [5 empty] | PASSED | FALSE |  | pending
2026-06-08 | WFI08 | SV216.04 | PQ3-Day1 | FALSE | 16-1-098 | Building 16 | CIP/SIP | WFI | 2026-06-09 | [5 empty] | PASSED | FALSE |  | pending
2026-06-09 | WFI03 | SV216.03 | PQ3-Day2 | FALSE | 16-1-096 | Building 16 | WASHING/TUNNEL-02 | WFI | 2026-06-09 | [5 empty] | PASSED | FALSE |  | pending
2026-06-09 | WFI04 | POU HE216.03 | PQ3-Day2 | FALSE | 16-1-082 | Building 16 | WASHING | WFI | 2026-06-09 | [5 empty] | PASSED | FALSE |  | pending
2026-06-09 | WFI05 | SV216.06 | PQ3-Day2 | FALSE | 16-1-082 | Building 16 | WASHING | WFI | 2026-06-09 | [5 empty] | PASSED | FALSE |  | pending
2026-06-10 | WFI01 | POU HE216.01 | PQ3-Day3 | FALSE | 16-1-107 | Building 16 | COMPOUNDING-01 | WFI | 2026-06-11 | [5 empty] | PASSED | FALSE |  | pending
2026-06-10 | WFI02 | POU HE216.02 | PQ3-Day3 | FALSE | 16-1-107 | Building 16 | COMPOUNDING-01 | WFI | 2026-06-11 | [5 empty] | PASSED | FALSE |  | pending
2026-06-11 | WFI06 | SV216.05 | PQ3-Day4 | FALSE | 16-1-110 | Building 16 | DISINFECTANT PREPARATION | WFI | 2026-06-11 | [5 empty] | PASSED | FALSE |  | pending
2026-06-11 | WFI09 | SV216.10 | PQ3-Day4 | FALSE | 16-1-105 | Building 16 | WASHING/TUNNEL-01 | WFI | 2026-06-11 | [5 empty] | PASSED | FALSE |  | pending
2026-06-12 | WFI10 | POU HE216.04 | PQ3-Day5 | FALSE | 16-1-114 | Building 16 | COMPOUNDING-02 | WFI | 2026-06-13 | [5 empty] | PASSED | FALSE |  | pending
2026-06-12 | WFI11 | POU HE216.05 | PQ3-Day5 | FALSE | 16-1-114 | Building 16 | COMPOUNDING-02 | WFI | 2026-06-13 | [5 empty] | PASSED | FALSE |  | pending
Formulas:
performedDate = [samplingDate]+1

## database
samplingPoint | samplingTag | location | noLocation | waterSystem | building | waterType | Criteria |  | waterType | Unit | Spec
BU19-14 | SV-14 | AFTER RO SYSTEM NO.12 SV14 | PROCESS WATER (B19) | GENERATION SYSTEM | Building 19 | PRW | 500 |  | PRW | cfu/ml | 500
BU19-15 | SV-15 | AFTER RO SYSTEM NO.12 SV15 | PROCESS WATER (B19) | GENERATION SYSTEM | Building 19 | PRW | 500 |  | RO water | cfu/ml | 500
GOSD01 | VB-05(10) | After Chlorine circulation tank (B10) | WATER SYSTEM (B10) | GENERATION SYSTEM | Building 10 | PRW | 500 |  | PW | cfu/ml | 100
GOSD02 | V50-60(10) | Before Cartridge filter 5 µm (B10) | WATER SYSTEM (B10) | GENERATION SYSTEM | Building 10 | PRW | 500 |  | WFI | cfu/100ml | 10
GOSD03 | V50-61(10) | After Cartridge filter 5 µm (B10) | WATER SYSTEM (B10) | GENERATION SYSTEM | Building 10 | PRW | 500
GOSD04 | V50-11C(10) | After RO (Before EDI) (B10) | WATER SYSTEM (B10) | GENERATION SYSTEM | Building 10 | RO water | 500
GOSD05 | V50-39(10) | After EDI (B10) | WATER SYSTEM (B10) | GENERATION SYSTEM | Building 10 | PW | 100
GOSD06 | SV113.01 | After Storage tank (B10) | WATER SYSTEM (B10) | GENERATION SYSTEM | Building 10 | PW | 100
GOSD07 | SV115.02 | After UV (B10) | WATER SYSTEM (B10) | GENERATION SYSTEM | Building 10 | PW | 100
GOSD08 | SV117.01 | Return loop (B10) | WATER SYSTEM (B10) | GENERATION SYSTEM | Building 10 | PW | 100
OSD01 | SV116.15 | CIP SKID-1 FOR BIN WASHING-1 | 10-4-012 | DISTRIBUTION LOOP SYSTEM | Building 10 | PW | 100
OSD02 | SV116.16 | WIP SKID-3 FOR GRANULATION POTENT | 10-4-012 | DISTRIBUTION LOOP SYSTEM | Building 10 | PW | 100
OSD03 | SV116.17 | CIP SKID-2 FOR BIN WASHING-1 | 10-4-012 | DISTRIBUTION LOOP SYSTEM | Building 10 | PW | 100
OSD04 | SV116.18 | WIP SKID-1 FOR GRANULATION NON POTENT | 10-4-012 | DISTRIBUTION LOOP SYSTEM | Building 10 | PW | 100
OSD05 | SV116.19 | WIP SKID-2 FOR GRANULATION NON POTENT | 10-4-012 | DISTRIBUTION LOOP SYSTEM | Building 10 | PW | 100
OSD06 | DV116.18 | WET GRANULATION-5 | 10-3-111 | DISTRIBUTION LOOP SYSTEM | Building 10 | PW | 100
OSD07 | DV116.16 | WET GRANULATION-2 | 10-3-107 | DISTRIBUTION LOOP SYSTEM | Building 10 | PW | 100
OSD08 | SV116.11 | WET GRANULATION-2 | 10-3-107 | DISTRIBUTION LOOP SYSTEM | Building 10 | PW | 100
OSD09 | DV116.14 | TOOL WASHING | 10-3-086 | DISTRIBUTION LOOP SYSTEM | Building 10 | PW | 100
OSD10 | SV116.09 | WASHING | 10-3-078 | DISTRIBUTION LOOP SYSTEM | Building 10 | PW | 100
OSD11 | DV116.13 | WASHING | 10-3-078 | DISTRIBUTION LOOP SYSTEM | Building 10 | PW | 100
OSD12 | DV116.12 | WASHING | 10-3-078 | DISTRIBUTION LOOP SYSTEM | Building 10 | PW | 100
OSD13 | DV116.25 | TOOL WASHING-P | 10-3-171 | DISTRIBUTION LOOP SYSTEM | Building 10 | PW | 100
OSD14 | DV116.24 | WET GRANULATION 1-P | 10-3-163 | DISTRIBUTION LOOP SYSTEM | Building 10 | PW | 100
OSD15 | DV116.23 | BINDER PREPARATION-P | 10-3-159 | DISTRIBUTION LOOP SYSTEM | Building 10 | PW | 100
OSD16 | DV116.21 | WASHING-P | 10-3-152 | DISTRIBUTION LOOP SYSTEM | Building 10 | PW | 100
OSD17 | DV116.22 | WASHING-P | 10-3-152 | DISTRIBUTION LOOP SYSTEM | Building 10 | PW | 100
OSD18 | SV116.13 | WASHING-P | 10-3-152 | DISTRIBUTION LOOP SYSTEM | Building 10 | PW | 100
OSD19 | DV116.20 | IPQC-1-P | 10-3-149 | DISTRIBUTION LOOP SYSTEM | Building 10 | PW | 100
OSD20 | DV116.19 | COATING SOLUTION PREP.-P | 10-3-143 | DISTRIBUTION LOOP SYSTEM | Building 10 | PW | 100
OSD21 | SV116.12 | COATING-P | 10-3-144 | DISTRIBUTION LOOP SYSTEM | Building 10 | PW | 100 | IPQC-2
OSD22 | SV116.05 | COATING ROOM-3 | 10-3-062 | DISTRIBUTION LOOP SYSTEM | Building 10 | PW | 100
OSD23 | SV116.04 | COATING ROOM-2 | 10-3-061 | DISTRIBUTION LOOP SYSTEM | Building 10 | PW | 100
OSD24 | DV116.09 | COATING SOLUTION PREP.-2 | 10-3-060 | DISTRIBUTION LOOP SYSTEM | Building 10 | PW | 100
OSD25 | DV116.08 | COATING SOLUTION PREP.-1 | 10-3-059 | DISTRIBUTION LOOP SYSTEM | Building 10 | PW | 100
OSD26 | SV116.03 | COATING ROOM-1 | 10-3-058 | DISTRIBUTION LOOP SYSTEM | Building 10 | PW | 100
OSD27 | DV116.17 | IPQC-2 | 10-3-117 | DISTRIBUTION LOOP SYSTEM | Building 10 | PW | 100
OSD28 | DV116.15 | BINDER PREPARATION | 10-3-104 | DISTRIBUTION LOOP SYSTEM | Building 10 | PW | 100
OSD29 | SV116.08 | COATING ROOM-6 | 10-3-067 | DISTRIBUTION LOOP SYSTEM | Building 10 | PW | 100
OSD30 | DV116.11 | COATING SOLUTION PREP.-4 | 10-3-066 | DISTRIBUTION LOOP SYSTEM | Building 10 | PW | 100
OSD31 | DV116.10 | COATING SOLUTION PREP.-3 | 10-3-065 | DISTRIBUTION LOOP SYSTEM | Building 10 | PW | 100
OSD32 | SV116.07 | COATING ROOM-5 | 10-3-064 | DISTRIBUTION LOOP SYSTEM | Building 10 | PW | 100
OSD33 | SV116.06 | COATING ROOM-4 | 10-3-063 | DISTRIBUTION LOOP SYSTEM | Building 10 | PW | 100
OSD34 | SV116.02 | SKID FOR BIN WASHING-2 | 10-2-037 | DISTRIBUTION LOOP SYSTEM | Building 10 | PW | 100
OSD35 | SV116.01 | INSTRUMENT-1 | 10-2-021 | DISTRIBUTION LOOP SYSTEM | Building 10 | PW | 100
OSD36 | DV116.03 | SAMPLE PREPARATION | 10-2-034 | DISTRIBUTION LOOP SYSTEM | Building 10 | PW | 100
OSD37 | DV116.06 | SAMPLE PREPARATION | 10-2-034 | DISTRIBUTION LOOP SYSTEM | Building 10 | PW | 100
OSD38 | DV116.07 | GLASS-WARE WASHING | 10-2-032 | DISTRIBUTION LOOP SYSTEM | Building 10 | PW | 100
OSD39 | DV116.05 | GLASS-WARE WASHING | 10-2-032 | DISTRIBUTION LOOP SYSTEM | Building 10 | PW | 100
OSD40 | DV116.04 | SKID FOR BIN WASHING-1 | 10-2-037 | DISTRIBUTION LOOP SYSTEM | Building 10 | PW | 100
OSD41 | DV116.02 | WASHING | 10-1-115 | DISTRIBUTION LOOP SYSTEM | Building 10 | PW | 100
OSD42 | DV116.01 | WASHING-P | 10-1-057 | DISTRIBUTION LOOP SYSTEM | Building 10 | PW | 100
OSD43 | DV116.26 | WATER SYSTEM ROOM | 10-4-015 | DISTRIBUTION LOOP SYSTEM | Building 10 | PW | 100
GOLD01 | VB-05 (12) | After Chlorine circulation tank | WATER SYSTEM (B12) | GENERATION SYSTEM | Building 12 | PRW | 500
GOLD02 | V50-61 (12) | After Cartridge filter 5 µm (B12) | WATER SYSTEM (B12) | GENERATION SYSTEM | Building 12 | PRW | 500
GOLD03 | V50-11C (12) | After RO (Before EDI) (B12) | WATER SYSTEM (B12) | GENERATION SYSTEM | Building 12 | RO water | 500
GOLD04 | V50-39 (12) | After EDI (B12) | WATER SYSTEM (B12) | GENERATION SYSTEM | Building 12 | PW | 100
GOLD05 | SV133.01 | After Storage tank (B12) | WATER SYSTEM (B12) | GENERATION SYSTEM | Building 12 | PW | 100
GOLD06 | SV135.02 | After UV (B12) | WATER SYSTEM (B12) | GENERATION SYSTEM | Building 12 | PW | 100
GOLD07 | SV137.01 | Return loop (B12) | WATER SYSTEM (B12) | GENERATION SYSTEM | Building 12 | PW | 100
OLD01 | DV136.17 | WASHING | 12-2-065 | DISTRIBUTION LOOP SYSTEM | Building 12 | PW | 100
OLD02 | SV136.16 | CIP 2 | 12-2-057 | DISTRIBUTION LOOP SYSTEM | Building 12 | PW | 100
OLD03 | SV136.12 | CIP 1 | 12-2-036 | DISTRIBUTION LOOP SYSTEM | Building 12 | PW | 100
OLD04 | SV136.07 | SYRUP PREPARATION | 12-2-034 | DISTRIBUTION LOOP SYSTEM | Building 12 | PW | 100
OLD05 | SV136.06 | SYRUP PREPARATION | 12-2-034 | DISTRIBUTION LOOP SYSTEM | Building 12 | PW | 100
OLD06 | SV136.09 | MFG 1 | 12-2-039 | DISTRIBUTION LOOP SYSTEM | Building 12 | PW | 100
OLD07 | SV136.10 | MFG 2 | 12-2-041 | DISTRIBUTION LOOP SYSTEM | Building 12 | PW | 100
OLD08 | SV136.11 | MFG 3 | 12-2-043 | DISTRIBUTION LOOP SYSTEM | Building 12 | PW | 100
OLD09 | SV136.13 | MFG 3 | 12-2-043 | DISTRIBUTION LOOP SYSTEM | Building 12 | PW | 100
OLD10 | SV136.15 | CIP 3 | 12-2-055 | DISTRIBUTION LOOP SYSTEM | Building 12 | PW | 100
OLD11 | SV136.08 | MFG 3 | 12-2-043 | DISTRIBUTION LOOP SYSTEM | Building 12 | PW | 100
OLD12 | SV136.03 | CAMPHORATED OPIUM TINCTURE | 12-2-032 | DISTRIBUTION LOOP SYSTEM | Building 12 | PW | 100
OLD13 | SV136.05 | CAMPHORATED OPIUM TINCTURE | 12-2-032 | DISTRIBUTION LOOP SYSTEM | Building 12 | PW | 100
OLD14 | SV136.04 | OPIUM TINCTURE | 12-2-030 | DISTRIBUTION LOOP SYSTEM | Building 12 | PW | 100
OLD15 | DV136.02 | ALCOHOL STORAGE | 12-2-028 | DISTRIBUTION LOOP SYSTEM | Building 12 | PW | 100
OLD16 | SV136.14 | MFG 4 | 12-2-045 | DISTRIBUTION LOOP SYSTEM | Building 12 | PW | 100
OLD17 | DV136.03 | IPQC | 12-2-053 | DISTRIBUTION LOOP SYSTEM | Building 12 | PW | 100
OLD18 | SV136.02 | LIQUORICE EXTRACT | 12-2-024 | DISTRIBUTION LOOP SYSTEM | Building 12 | PW | 100
OLD19 | DV136.01 | SUGAR TRANSFERRING | 12-1-035 | DISTRIBUTION LOOP SYSTEM | Building 12 | PW | 100
OLD20 | DV136.16 | WASHING | 12-1-064 | DISTRIBUTION LOOP SYSTEM | Building 12 | PW | 100
OLD21 | DV136.15 | GLASSWARE WASHING 2 | 12-3-078 | DISTRIBUTION LOOP SYSTEM | Building 12 | PW | 100
OLD22 | DV136.13 | STERILIZATION | 12-3-057 | DISTRIBUTION LOOP SYSTEM | Building 12 | PW | 100
OLD23 | SV136.18 | AUTOCLAVE | 12-3-059 | DISTRIBUTION LOOP SYSTEM | Building 12 | PW | 100
OLD24 | DV136.11 | AUTOCLAVE | 12-3-059 | DISTRIBUTION LOOP SYSTEM | Building 12 | PW | 100
OLD25 | DV136.12 | MEDIA PREPARATION | 12-3-056 | DISTRIBUTION LOOP SYSTEM | Building 12 | PW | 100
OLD26 | DV136.10 | MEDIA PREPARATION | 12-3-056 | DISTRIBUTION LOOP SYSTEM | Building 12 | PW | 100
OLD27 | DV136.14 | DECONTAMINATION | 12-3-074 | DISTRIBUTION LOOP SYSTEM | Building 12 | PW | 100
OLD28 | DV136.18 | GLASSWARE WASHING 1 | 12-3-037 | DISTRIBUTION LOOP SYSTEM | Building 12 | PW | 100
OLD29 | DV136.05 | GLASSWARE WASHING 1 | 12-3-037 | DISTRIBUTION LOOP SYSTEM | Building 12 | PW | 100
OLD30 | DV136.06 | GLASSWARE WASHING 1 | 12-3-037 | DISTRIBUTION LOOP SYSTEM | Building 12 | PW | 100
OLD31 | DV136.07 | INSTRUMENT 7 | 12-3-039 | DISTRIBUTION LOOP SYSTEM | Building 12 | PW | 100
OLD32 | DV136.08 | SAMPLE PREPARATION | 12-3-042 | DISTRIBUTION LOOP SYSTEM | Building 12 | PW | 100
OLD33 | DV136.09 | SAMPLE PREPARATION | 12-3-042 | DISTRIBUTION LOOP SYSTEM | Building 12 | PW | 100
OLD34 | DV136.04 | WATER SYSTEM ROOM | 12-2-077 | DISTRIBUTION LOOP SYSTEM | Building 12 | PW | 100
GOCL01 | VB-05 (16) | After Chlorine circulation tank (B16) | WATER SYSTEM (B16) | GENERATION SYSTEM | Building 16 | PRW | 500
GOCL02 | V50-61 (16) | After Cartridge filter 5 µm (B16) | WATER SYSTEM (B16) | GENERATION SYSTEM | Building 16 | PRW | 500
GOCL03 | V50-11C (16) | After RO (Before EDI) (B16) | WATER SYSTEM (B16) | GENERATION SYSTEM | Building 16 | RO water | 500
GOCL04 | V50-39 (16) | After EDI (B16) | WATER SYSTEM (B16) | GENERATION SYSTEM | Building 16 | PW | 100
GOCL05 | SV123.01 | After Storage tank (B16) | WATER SYSTEM (B16) | GENERATION SYSTEM | Building 16 | PW | 100
GOCL06 | SV125.01 | After Pump | WATER SYSTEM (B16) | GENERATION SYSTEM | Building 16 | PW | 100
GOCL07 | SV125.02 | After UV (B16) | WATER SYSTEM (B16) | GENERATION SYSTEM | Building 16 | PW | 100
GOCL08 | SV127.01 | Return loop (B16) | WATER SYSTEM (B16) | GENERATION SYSTEM | Building 16 | PW | 100
OCL01 | DV126.02 | WASHING | 16-1-082 | DISTRIBUTION LOOP SYSTEM | Building 16 | PW | 100
OCL02 | DV126.01 | WASHING | 16-1-082 | DISTRIBUTION LOOP SYSTEM | Building 16 | PW | 100
OCL03 | SV126.02 | CIP/SIP (EQUIPMENT REQUIREMENT – 200L) | 16-1-098 | DISTRIBUTION LOOP SYSTEM | Building 16 | PW | 100
OCL04 | DV126.03 | CIP/SIP (SINK WASHING) | 16-1-098 | DISTRIBUTION LOOP SYSTEM | Building 16 | PW | 100
OCL05 | SV126.01 | LINEN WASHING | 16-1-092 | DISTRIBUTION LOOP SYSTEM | Building 16 | PW | 100
OCL06 | SV126.06 | MFG 1 | 16-3-067 | DISTRIBUTION LOOP SYSTEM | Building 16 | PW | 100
OCL07 | SV126.21 | CIP 1 (EQUIPMENT REQUIREMENT) | 16-3-090 | DISTRIBUTION LOOP SYSTEM | Building 16 | PW | 100
OCL08 | DV126.09 | CIP 1 (ZINK WASHING) | 16-3-090 | DISTRIBUTION LOOP SYSTEM | Building 16 | PW | 100
OCL09 | DV126.10 | MFG 2 | 16-3-069 | DISTRIBUTION LOOP SYSTEM | Building 16 | PW | 100
OCL10 | DV126.06 | MFG 2 | 16-3-069 | DISTRIBUTION LOOP SYSTEM | Building 16 | PW | 100
OCL11 | SV126.10 | MFG 3 (1200L) | 16-3-071 | DISTRIBUTION LOOP SYSTEM | Building 16 | PW | 100
OCL12 | SV126.09 | MFG 3 (5000L) | 16-3-071 | DISTRIBUTION LOOP SYSTEM | Building 16 | PW | 100
OCL13 | SV126.19 | CIP 2 (EQUIPMENT REQUIREMENT) | 16-3-087 | DISTRIBUTION LOOP SYSTEM | Building 16 | PW | 100
OCL14 | DV126.11 | MFG 4 (5000L) | 16-3-073 | DISTRIBUTION LOOP SYSTEM | Building 16 | PW | 100
OCL15 | SV126.14 | MFG 4 (400L) | 16-3-073 | DISTRIBUTION LOOP SYSTEM | Building 16 | PW | 100
OCL16 | SV126.18 | CIP 3 (EQUIPMENT REQUIREMENT) | 16-3-085 | DISTRIBUTION LOOP SYSTEM | Building 16 | PW | 100
OCL17 | SV126.15 | MFG 5 PROCESS (2000L) | 16-3-075 | DISTRIBUTION LOOP SYSTEM | Building 16 | PW | 100
OCL18 | DV126.08 | MFG 6 | 16-3-077 | DISTRIBUTION LOOP SYSTEM | Building 16 | PW | 100
OCL19 | DV126.07 | MFG 6 | 16-3-077 | DISTRIBUTION LOOP SYSTEM | Building 16 | PW | 100
OCL20 | SV126.05 | LINEN WASHING | 16-3-049 | DISTRIBUTION LOOP SYSTEM | Building 16 | PW | 100
OCL21 | DV126.05 | WASHING | 16-3-054 | DISTRIBUTION LOOP SYSTEM | Building 16 | PW | 100
OCL22 | SV126.03 | WATER SYSTEM (WFI) | 16-2-010 | DISTRIBUTION LOOP SYSTEM | Building 16 | PW | 100
OCL23 | SV126.04 | WATER SYSTEM (PSG) | 16-2-010 | DISTRIBUTION LOOP SYSTEM | Building 16 | PW | 100
OCL24 | DV126.04 | WATER SYSTEM (PW) | 16-2-010 | DISTRIBUTION LOOP SYSTEM | Building 16 | PW | 100
GWFI01 | V12-4 | AFTER WFI GENERATOR | 16-2-010 | GENERATION SYSTEM | Building 16 | WFI | 10
GWFI02 | SV213.01 | AFTER STORAGE TANK | 16-2-010 | DISTRIBUTION LOOP SYSTEM | Building 16 | WFI | 10
GWFI03 | SV217.01 | RETURN LOOP | 16-2-010 | DISTRIBUTION LOOP SYSTEM | Building 16 | WFI | 10
WFI01 | POU HE216.01 | COMPOUNDING-01 | 16-1-107 | DISTRIBUTION LOOP SYSTEM | Building 16 | WFI | 10
WFI02 | POU HE216.02 | COMPOUNDING-01 | 16-1-107 | DISTRIBUTION LOOP SYSTEM | Building 16 | WFI | 10
WFI03 | SV216.03 | WASHING/TUNNEL-02 | 16-1-096 | DISTRIBUTION LOOP SYSTEM | Building 16 | WFI | 10
WFI04 | POU HE216.03 | WASHING | 16-1-082 | DISTRIBUTION LOOP SYSTEM | Building 16 | WFI | 10
WFI05 | SV216.06 | WASHING | 16-1-082 | DISTRIBUTION LOOP SYSTEM | Building 16 | WFI | 10
WFI06 | SV216.05 | DISINFECTANT PREPARATION | 16-1-110 | DISTRIBUTION LOOP SYSTEM | Building 16 | WFI | 10
WFI07 | SV216.02 | CIP/SIP | 16-1-098 | DISTRIBUTION LOOP SYSTEM | Building 16 | WFI | 10
WFI08 | SV216.04 | CIP/SIP | 16-1-098 | DISTRIBUTION LOOP SYSTEM | Building 16 | WFI | 10
WFI09 | SV216.10 | WASHING/TUNNEL-01 | 16-1-105 | DISTRIBUTION LOOP SYSTEM | Building 16 | WFI | 10
WFI10 | POU HE216.04 | COMPOUNDING-02 | 16-1-114 | DISTRIBUTION LOOP SYSTEM | Building 16 | WFI | 10
WFI11 | POU HE216.05 | COMPOUNDING-02 | 16-1-114 | DISTRIBUTION LOOP SYSTEM | Building 16 | WFI | 10
GPUS01 | V12-14 | After PUS Generator | WATER SYSTEM (B16) | GENERATION SYSTEM | Building 16 | PUS | #N/A
PUS01 | BV319.33 | TERMINAL STERILIZER-01 | 16-1-061 | DISTRIBUTION LOOP SYSTEM | Building 16 | PUS | #N/A
PUS02 | BV319.56 | TERMINAL STERILIZER-02 | 16-1-050 | DISTRIBUTION LOOP SYSTEM | Building 16 | PUS | #N/A
PUS03 | BV319.57 | FILTRATION-01 | 16-1-083 | DISTRIBUTION LOOP SYSTEM | Building 16 | PUS | #N/A
PUS04 | BV319.58 | COMPOUNDING-01 | 16-1-107 | DISTRIBUTION LOOP SYSTEM | Building 16 | PUS | #N/A
PUS05 | BV319.59 | CIP / SIP | 16-1-098 | DISTRIBUTION LOOP SYSTEM | Building 16 | PUS | #N/A
PUS06 | BV319.60 | COMPONENT PREPARATION | 16-1-111 | DISTRIBUTION LOOP SYSTEM | Building 16 | PUS | #N/A
PUS07 | BV319.55 | COMPOUNDING-02 | 16-1-114 | DISTRIBUTION LOOP SYSTEM | Building 16 | PUS | #N/A
PUS08 | BV319.45 | FILTRATION-02 | 16-1-077 | DISTRIBUTION LOOP SYSTEM | Building 16 | PUS | #N/A

## ลงรูป
https://drive.google.com/drive/folders/1ee7LRvItfyxSZzd-Q-yVXdDGrdT5co9o

## allData (hidden)
samplingDate | samplingPoint | samplingTag | recordStatus | noLocation | building | location | waterType | performedDate | determinedDate | result1 | result2 | resultAvg | comment | criteria | statusResult | Column 1
2025-01-06 | OSD06 | DV116.18 | Routine | 10-3-111 | Building 10 | WET GRANULATION-5 | PW | 2025-01-07 | 2025-01-10 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-01-06 | OSD07 | DV116.16 | Routine | 10-3-107 | Building 10 | WET GRANULATION-2 | PW | 2025-01-07 | 2025-01-10 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-01-06 | OSD09 | DV116.14 | Routine | 10-3-086 | Building 10 | TOOL WASHING | PW | 2025-01-07 | 2025-01-10 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-01-06 | OSD10 | SV116.09 | Routine | 10-3-078 | Building 10 | WASHING | PW | 2025-01-07 | 2025-01-10 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-01-06 | OSD11 | DV116.13 | Routine | 10-3-078 | Building 10 | WASHING | PW | 2025-01-07 | 2025-01-10 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-01-06 | OSD12 | DV116.12 | Routine | 10-3-078 | Building 10 | WASHING | PW | 2025-01-07 | 2025-01-10 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-01-06 | OSD01 | SV116.15 | Routine | 10-4-012 | Building 10 | CIP SKID-1 FOR BIN WASHING-1 | PW | 2025-01-07 | 2025-01-10 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-01-06 | OSD03 | SV116.17 | Routine | 10-4-012 | Building 10 | CIP SKID-2 FOR BIN WASHING-1 | PW | 2025-01-07 | 2025-01-10 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-01-06 | OSD27 | DV116.17 | Routine | 10-3-117 | Building 10 | IPQC-2 | PW | 2025-01-07 | 2025-01-10 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-01-06 | OSD28 | DV116.15 | Routine | 10-3-104 | Building 10 | BINDER PREPARATION | PW | 2025-01-07 | 2025-01-10 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-01-06 | GOSD01 | VB-05(10) | Routine | WATER SYSTEM (B10) | Building 10 | After Chlorine circulation tank (B10) | PRW | 2025-01-07 | 2025-01-10 | 0 | 0 | 0 | NA | 500 | PASSED | WA
2025-01-06 | GOSD02 | V50-60(10) | Routine | WATER SYSTEM (B10) | Building 10 | Before Cartridge filter 5 µm (B10) | PRW | 2025-01-07 | 2025-01-10 | 804 | 732 | 768 | NA | 500 | NOT-PASSED | WA
2025-01-06 | GOSD03 | V50-61(10) | Routine | WATER SYSTEM (B10) | Building 10 | After Cartridge filter 5 µm (B10) | PRW | 2025-01-07 | 2025-01-10 | 248 | 279 | 264 | NA | 500 | PASSED | WA
2025-01-06 | GOSD04 | V50-11C(10) | Routine | WATER SYSTEM (B10) | Building 10 | After RO (Before EDI) (B10) | RO water | 2025-01-07 | 2025-01-10 | 0 | 0 | 0 | NA | 500 | PASSED | WA
2025-01-06 | GOSD05 | V50-39(10) | Routine | WATER SYSTEM (B10) | Building 10 | After EDI (B10) | PW | 2025-01-07 | 2025-01-10 | 0 | 0 | 0 | NA | 100 | PASSED | WA
2025-01-17 | OSD31 | DV116.10 | Routine | 10-3-065 | Building 10 | COATING SOLUTION PREP.-3 | PW | 2025-01-18 | 2025-01-21 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-01-17 | OSD32 | SV116.07 | Routine | 10-3-064 | Building 10 | COATING ROOM-5 | PW | 2025-01-18 | 2025-01-21 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-01-17 | OSD38 | DV116.07 | Routine | 10-2-032 | Building 10 | GLASS-WARE WASHING | PW | 2025-01-18 | 2025-01-21 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-01-17 | OSD39 | DV116.05 | Routine | 10-2-032 | Building 10 | GLASS-WARE WASHING | PW | 2025-01-18 | 2025-01-21 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-01-17 | OSD23 | SV116.04 | Routine | 10-3-061 | Building 10 | COATING ROOM-2 | PW | 2025-01-18 | 2025-01-21 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-01-17 | OSD29 | SV116.08 | Routine | 10-3-067 | Building 10 | COATING ROOM-6 | PW | 2025-01-18 | 2025-01-21 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-01-17 | OSD40 | DV116.04 | Routine | 10-2-037 | Building 10 | SKID FOR BIN WASHING-1 | PW | 2025-01-18 | 2025-01-21 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-01-17 | OSD37 | DV116.06 | Routine | 10-2-034 | Building 10 | SAMPLE PREPARATION | PW | 2025-01-18 | 2025-01-21 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-01-17 | OSD22 | SV116.05 | Routine | 10-3-062 | Building 10 | COATING ROOM-3 | PW | 2025-01-18 | 2025-01-21 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-01-17 | OSD26 | SV116.03 | Routine | 10-3-058 | Building 10 | COATING ROOM-1 | PW | 2025-01-18 | 2025-01-21 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-01-17 | OSD24 | DV116.09 | Routine | 10-3-060 | Building 10 | COATING SOLUTION PREP.-2 | PW | 2025-01-18 | 2025-01-21 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-01-17 | OSD33 | SV116.06 | Routine | 10-3-063 | Building 10 | COATING ROOM-4 | PW | 2025-01-18 | 2025-01-21 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-01-17 | OSD25 | DV116.08 | Routine | 10-3-059 | Building 10 | COATING SOLUTION PREP.-1 | PW | 2025-01-18 | 2025-01-21 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-01-17 | OSD30 | DV116.11 | Routine | 10-3-066 | Building 10 | COATING SOLUTION PREP.-4 | PW | 2025-01-18 | 2025-01-21 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-01-17 | OSD36 | DV116.03 | Routine | 10-2-034 | Building 10 | SAMPLE PREPARATION | PW | 2025-01-18 | 2025-01-21 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-01-17 | GOSD02 | V50-60(10) | Routine | WATER SYSTEM (B10) | Building 10 | Before Cartridge filter 5 µm (B10) | PRW | 2025-01-18 | 2025-01-21 | 999 | 999 | 999 | NA | 500 | NOT-PASSED | WA
2025-01-17 | GOSD03 | V50-61(10) | Routine | WATER SYSTEM (B10) | Building 10 | After Cartridge filter 5 µm (B10) | PRW | 2025-01-18 | 2025-01-21 | 999 | 999 | 999 | NA | 500 | NOT-PASSED | WA
2025-01-17 | GOSD06 | SV113.01 | Routine | WATER SYSTEM (B10) | Building 10 | After Storage tank (B10) | PW | 2025-01-18 | 2025-01-21 | 0 | 0 | 0 | NA | 100 | PASSED | WA
2025-01-17 | GOSD07 | SV115.02 | Routine | WATER SYSTEM (B10) | Building 10 | After UV (B10) | PW | 2025-01-18 | 2025-01-21 | 0 | 0 | 0 | NA | 100 | PASSED | WA
2025-01-17 | GOSD08 | SV117.01 | Routine | WATER SYSTEM (B10) | Building 10 | Return loop (B10) | PW | 2025-01-18 | 2025-01-21 | 0 | 0 | 0 | NA | 100 | PASSED | WA
2025-01-20 | GOSD01 | VB-05(10) | Routine | WATER SYSTEM (B10) | Building 10 | After Chlorine circulation tank (B10) | PRW | 2025-01-21 | 2025-01-24 | 0 | 0 | 0 | NA | 500 | PASSED | WA
2025-01-20 | BU19-14 | SV-14 | Routine | PROCESS WATER (B19) | Building 19 | AFTER RO SYSTEM NO.12 SV14 | PRW | 2025-01-21 | 2025-01-24 | 0 | 0 | 0 | NA | 500 | PASSED | PR
2025-01-20 | OSD42 | DV116.01 | Routine | 10-1-057 | Building 10 | WASHING-P | PW | 2025-01-21 | 2025-01-24 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-01-20 | OSD41 | DV116.02 | Routine | 10-1-115 | Building 10 | WASHING | PW | 2025-01-21 | 2025-01-24 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-01-20 | OSD20 | DV116.19 | Routine | 10-3-143 | Building 10 | COATING SOLUTION PREP.-P | PW | 2025-01-21 | 2025-01-24 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-01-20 | OSD19 | DV116.20 | Routine | 10-3-149 | Building 10 | IPQC-1-P | PW | 2025-01-21 | 2025-01-24 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-01-20 | OSD16 | DV116.21 | Routine | 10-3-152 | Building 10 | WASHING-P | PW | 2025-01-21 | 2025-01-24 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-01-20 | OSD17 | DV116.22 | Routine | 10-3-152 | Building 10 | WASHING-P | PW | 2025-01-21 | 2025-01-24 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-01-20 | OSD15 | DV116.23 | Routine | 10-3-159 | Building 10 | BINDER PREPARATION-P | PW | 2025-01-21 | 2025-01-24 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-01-20 | OSD14 | DV116.24 | Routine | 10-3-163 | Building 10 | WET GRANULATION 1-P | PW | 2025-01-21 | 2025-01-24 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-01-20 | OSD13 | DV116.25 | Routine | 10-3-171 | Building 10 | TOOL WASHING-P | PW | 2025-01-21 | 2025-01-24 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-01-20 | OSD21 | SV116.12 | Routine | 10-3-144 | Building 10 | COATING-P | PW | 2025-01-21 | 2025-01-24 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-01-20 | OSD21 | SV116.12 | Routine | 10-3-144 | Building 10 | COATING-P | PW | 2025-01-21 | 2025-01-24 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-01-20 | OSD18 | SV116.13 | Routine | 10-3-152 | Building 10 | WASHING-P | PW | 2025-01-21 | 2025-01-24 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-01-20 | GOSD02 | V50-60(10) | Routine | WATER SYSTEM (B10) | Building 10 | Before Cartridge filter 5 µm (B10) | PRW | 2025-01-21 | 2025-01-24 | 999 | 999 | 999 | NA | 500 | NOT-PASSED | WA
2025-01-20 | GOSD03 | V50-61(10) | Routine | WATER SYSTEM (B10) | Building 10 | After Cartridge filter 5 µm (B10) | PRW | 2025-01-21 | 2025-01-24 | 999 | 999 | 999 | NA | 500 | NOT-PASSED | WA
2025-01-20 | GOSD04 | V50-11C(10) | Routine | WATER SYSTEM (B10) | Building 10 | After RO (Before EDI) (B10) | RO water | 2025-01-21 | 2025-01-24 | 0 | 0 | 0 | NA | 500 | PASSED | WA
2025-01-20 | GOSD04 | V50-11C(10) | Routine | WATER SYSTEM (B10) | Building 10 | After RO (Before EDI) (B10) | RO water | 2025-01-21 | 2025-01-24 | 0 | 0 | 0 | NA | 500 | PASSED | WA
2025-01-20 | GOSD05 | V50-39(10) | Routine | WATER SYSTEM (B10) | Building 10 | After EDI (B10) | PW | 2025-01-21 | 2025-01-24 | 0 | 0 | 0 | NA | 100 | PASSED | WA
2025-01-27 | OSD43 | DV116.26 | Routine | 10-4-015 | Building 10 | WATER SYSTEM ROOM | PW | 2025-01-28 | 2025-01-31 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-01-27 | OSD01 | SV116.15 | Routine | 10-4-012 | Building 10 | CIP SKID-1 FOR BIN WASHING-1 | PW | 2025-01-28 | 2025-01-31 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-01-27 | OSD02 | SV116.16 | Routine | 10-4-012 | Building 10 | WIP SKID-3 FOR GRANULATION POTENT | PW | 2025-01-28 | 2025-01-31 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-01-27 | OSD03 | SV116.17 | Routine | 10-4-012 | Building 10 | CIP SKID-2 FOR BIN WASHING-1 | PW | 2025-01-28 | 2025-01-31 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-01-27 | OSD04 | SV116.18 | Routine | 10-4-012 | Building 10 | WIP SKID-1 FOR GRANULATION NON POTENT | PW | 2025-01-28 | 2025-01-31 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-01-27 | OSD05 | SV116.19 | Routine | 10-4-012 | Building 10 | WIP SKID-2 FOR GRANULATION NON POTENT | PW | 2025-01-28 | 2025-01-31 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-01-27 | OSD08 | SV116.11 | Routine | 10-3-107 | Building 10 | WET GRANULATION-2 | PW | 2025-01-28 | 2025-01-31 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-01-27 | OSD35 | SV116.01 | Routine | 10-2-021 | Building 10 | INSTRUMENT-1 | PW | 2025-01-28 | 2025-01-31 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-01-27 | OSD34 | SV116.02 | Routine | 10-2-037 | Building 10 | SKID FOR BIN WASHING-2 | PW | 2025-01-28 | 2025-01-31 | 0 | 0 | 0 | w/o-Tube | 100 | PASSED | 10
2025-01-27 | OSD34 | SV116.02 | Routine | 10-2-037 | Building 10 | SKID FOR BIN WASHING-2 | PW | 2025-01-28 | 2025-01-31 | 0 | 0 | 0 | with-tube | 100 | PASSED | 10
2025-01-27 | GOSD02 | V50-60(10) | Routine | WATER SYSTEM (B10) | Building 10 | Before Cartridge filter 5 µm (B10) | PRW | 2025-01-28 | 2025-01-31 | 999 | 999 | 999 | NA | 500 | NOT-PASSED | WA
2025-01-27 | GOSD03 | V50-61(10) | Routine | WATER SYSTEM (B10) | Building 10 | After Cartridge filter 5 µm (B10) | PRW | 2025-01-28 | 2025-01-31 | 999 | 999 | 999 | NA | 500 | NOT-PASSED | WA
2025-01-27 | GOSD06 | SV113.01 | Routine | WATER SYSTEM (B10) | Building 10 | After Storage tank (B10) | PW | 2025-01-28 | 2025-01-31 | 0 | 0 | 0 | NA | 100 | PASSED | WA
2025-01-27 | GOSD07 | SV115.02 | Routine | WATER SYSTEM (B10) | Building 10 | After UV (B10) | PW | 2025-01-28 | 2025-01-31 | 0 | 0 | 0 | NA | 100 | PASSED | WA
2025-01-27 | GOSD08 | SV117.01 | Routine | WATER SYSTEM (B10) | Building 10 | Return loop (B10) | PW | 2025-01-28 | 2025-01-31 | 0 | 0 | 0 | NA | 100 | PASSED | WA
2025-02-03 | GOCL02 | V50-61 (16) | Routine | WATER SYSTEM (B16) | Building 16 | After Cartridge filter 5 µm (B16) | PRW | 2025-02-04 | 2025-02-07 | 999 | 999 | 999 | NA | 500 | NOT-PASSED | WA
2025-02-03 | GOCL0A | #N/A | Routine | V50-60(16) | #N/A | BEFORE CARTRIDGE FILTER 5 MCM | PRW | 2025-02-04 | 2025-02-07 | 999 | 999 | 999 | NA | 500 | NOT-PASSED | V5
2025-02-03 | GOSD01 | VB-05(10) | Routine | WATER SYSTEM (B10) | Building 10 | After Chlorine circulation tank (B10) | PRW | 2025-02-04 | 2025-02-07 | 0 | 0 | 0 | NA | 500 | PASSED | WA
2025-02-03 | OSD06 | DV116.18 | Routine | 10-3-111 | Building 10 | WET GRANULATION-5 | PW | 2025-02-04 | 2025-02-07 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-02-03 | OSD07 | DV116.16 | Routine | 10-3-107 | Building 10 | WET GRANULATION-2 | PW | 2025-02-04 | 2025-02-07 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-02-03 | OSD09 | DV116.14 | Routine | 10-3-086 | Building 10 | TOOL WASHING | PW | 2025-02-04 | 2025-02-07 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-02-03 | OSD10 | SV116.09 | Routine | 10-3-078 | Building 10 | WASHING | PW | 2025-02-04 | 2025-02-07 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-02-03 | OSD11 | DV116.13 | Routine | 10-3-078 | Building 10 | WASHING | PW | 2025-02-04 | 2025-02-07 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-02-03 | OSD08 | SV116.11 | Routine | 10-3-107 | Building 10 | WET GRANULATION-2 | PW | 2025-02-04 | 2025-02-07 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-02-03 | OSD12 | DV116.12 | Routine | 10-3-078 | Building 10 | WASHING | PW | 2025-02-04 | 2025-02-07 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-02-03 | OSD28 | DV116.15 | Routine | 10-3-104 | Building 10 | BINDER PREPARATION | PW | 2025-02-04 | 2025-02-07 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-02-03 | OSD27 | DV116.17 | Routine | 10-3-117 | Building 10 | IPQC-2 | PW | 2025-02-04 | 2025-02-07 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-02-03 | OSD34 | SV116.02 | Routine | 10-2-037 | Building 10 | SKID FOR BIN WASHING-2 | PW | 2025-02-04 | 2025-02-07 | 0 | 0 | 0 | w/o-Tube | 100 | PASSED | 10
2025-02-03 | OSD34 | SV116.02 | Routine | 10-2-037 | Building 10 | SKID FOR BIN WASHING-2 | PW | 2025-02-04 | 2025-02-07 | 0 | 0 | 0 | with-tube | 100 | PASSED | 10
2025-02-03 | GOSD02 | V50-60(10) | Routine | WATER SYSTEM (B10) | Building 10 | Before Cartridge filter 5 µm (B10) | PRW | 2025-02-04 | 2025-02-07 | 999 | 999 | 999 | NA | 500 | NOT-PASSED | WA
2025-02-03 | GOSD03 | V50-61(10) | Routine | WATER SYSTEM (B10) | Building 10 | After Cartridge filter 5 µm (B10) | PRW | 2025-02-04 | 2025-02-07 | 999 | 999 | 999 | NA | 500 | NOT-PASSED | WA
2025-02-03 | GOSD04 | V50-11C(10) | Routine | WATER SYSTEM (B10) | Building 10 | After RO (Before EDI) (B10) | RO water | 2025-02-04 | 2025-02-07 | 0 | 0 | 0 | NA | 500 | PASSED | WA
2025-02-03 | GOSD05 | V50-39(10) | Routine | WATER SYSTEM (B10) | Building 10 | After EDI (B10) | PW | 2025-02-04 | 2025-02-07 | 0 | 0 | 0 | NA | 100 | PASSED | WA
2025-02-10 | GOCL04 | V50-39 (16) | Routine | WATER SYSTEM (B16) | Building 16 | After EDI (B16) | PW | 2025-02-11 | 2025-02-14 | 0 | 0 | 0 | NA | 500 | PASSED | WA
2025-02-10 | GOCL05 | SV123.01 | Routine | WATER SYSTEM (B16) | Building 16 | After Storage tank (B16) | PW | 2025-02-11 | 2025-02-14 | 0 | 0 | 0 | NA | 100 | PASSED | WA
2025-02-10 | GOCL06 | SV125.01 | Routine | WATER SYSTEM (B16) | Building 16 | After Pump | PW | 2025-02-11 | 2025-02-14 | 0 | 0 | 0 | NA | 100 | PASSED | WA
2025-02-10 | GOSD01 | VB-05(10) | Routine | WATER SYSTEM (B10) | Building 10 | After Chlorine circulation tank (B10) | PRW | 2025-02-11 | 2025-02-14 | 0 | 0 | 0 | NA | 500 | PASSED | WA
2025-02-10 | OSD34 | SV116.02 | Routine | 10-2-037 | Building 10 | SKID FOR BIN WASHING-2 | PW | 2025-02-11 | 2025-02-14 | 0 | 0 | 0 | with-tube | 100 | PASSED | 10
2025-02-10 | OSD34 | SV116.02 | Routine | 10-2-037 | Building 10 | SKID FOR BIN WASHING-2 | PW | 2025-02-11 | 2025-02-14 | 0 | 0 | 0 | w/o-Tube | 100 | PASSED | 10
2025-02-10 | GOSD02 | V50-60(10) | Routine | WATER SYSTEM (B10) | Building 10 | Before Cartridge filter 5 µm (B10) | PRW | 2025-02-11 | 2025-02-14 | 69 | 78 | 74 | NA | 500 | PASSED | WA
2025-02-10 | OSD21 | SV116.12 | Routine | 10-3-144 | Building 10 | COATING-P | PW | 2025-02-11 | 2025-02-14 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-02-10 | OSD18 | SV116.13 | Routine | 10-3-152 | Building 10 | WASHING-P | PW | 2025-02-11 | 2025-02-14 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-02-10 | OSD42 | DV116.01 | Routine | 10-1-057 | Building 10 | WASHING-P | PW | 2025-02-11 | 2025-02-14 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-02-10 | OSD41 | DV116.02 | Routine | 10-1-115 | Building 10 | WASHING | PW | 2025-02-11 | 2025-02-14 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-02-10 | OSD20 | DV116.19 | Routine | 10-3-143 | Building 10 | COATING SOLUTION PREP.-P | PW | 2025-02-11 | 2025-02-14 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-02-10 | OSD19 | DV116.20 | Routine | 10-3-149 | Building 10 | IPQC-1-P | PW | 2025-02-11 | 2025-02-14 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-02-10 | OSD16 | DV116.21 | Routine | 10-3-152 | Building 10 | WASHING-P | PW | 2025-02-11 | 2025-02-14 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-02-10 | OSD17 | DV116.22 | Routine | 10-3-152 | Building 10 | WASHING-P | PW | 2025-02-11 | 2025-02-14 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-02-10 | OSD15 | DV116.23 | Routine | 10-3-159 | Building 10 | BINDER PREPARATION-P | PW | 2025-02-11 | 2025-02-14 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-02-10 | OSD14 | DV116.24 | Routine | 10-3-163 | Building 10 | WET GRANULATION 1-P | PW | 2025-02-11 | 2025-02-14 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-02-10 | OSD13 | DV116.25 | Routine | 10-3-171 | Building 10 | TOOL WASHING-P | PW | 2025-02-11 | 2025-02-14 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-02-10 | GOSD03 | V50-61(10) | Routine | WATER SYSTEM (B10) | Building 10 | After Cartridge filter 5 µm (B10) | PRW | 2025-02-11 | 2025-02-14 | 118 | 131 | 125 | NA | 500 | PASSED | WA
2025-02-10 | GOSD06 | SV113.01 | Routine | WATER SYSTEM (B10) | Building 10 | After Storage tank (B10) | PW | 2025-02-11 | 2025-02-14 | 0 | 0 | 0 | NA | 100 | PASSED | WA
2025-02-10 | GOSD07 | SV115.02 | Routine | WATER SYSTEM (B10) | Building 10 | After UV (B10) | PW | 2025-02-11 | 2025-02-14 | 0 | 0 | 0 | NA | 100 | PASSED | WA
2025-02-10 | GOSD08 | SV117.01 | Routine | WATER SYSTEM (B10) | Building 10 | Return loop (B10) | PW | 2025-02-11 | 2025-02-14 | 13 | 8 | 11 | NA | 100 | PASSED | WA
2025-02-17 | GOSD01 | VB-05(10) | Routine | WATER SYSTEM (B10) | Building 10 | After Chlorine circulation tank (B10) | PRW | 2025-02-18 | 2025-02-21 | 1 | 0 | 1 | NA | 500 | PASSED | WA
2025-02-17 | GOSD02 | V50-60(10) | Routine | WATER SYSTEM (B10) | Building 10 | Before Cartridge filter 5 µm (B10) | PRW | 2025-02-18 | 2025-02-21 | 264 | 21 | 143 | NA | 500 | PASSED | WA
2025-02-17 | OSD22 | SV116.05 | Routine | 10-3-062 | Building 10 | COATING ROOM-3 | PW | 2025-02-18 | 2025-02-21 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-02-17 | OSD23 | SV116.04 | Routine | 10-3-061 | Building 10 | COATING ROOM-2 | PW | 2025-02-18 | 2025-02-21 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-02-17 | OSD24 | DV116.09 | Routine | 10-3-060 | Building 10 | COATING SOLUTION PREP.-2 | PW | 2025-02-18 | 2025-02-21 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-02-17 | OSD25 | DV116.08 | Routine | 10-3-059 | Building 10 | COATING SOLUTION PREP.-1 | PW | 2025-02-18 | 2025-02-21 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-02-17 | OSD26 | SV116.03 | Routine | 10-3-058 | Building 10 | COATING ROOM-1 | PW | 2025-02-18 | 2025-02-21 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-02-17 | OSD29 | SV116.08 | Routine | 10-3-067 | Building 10 | COATING ROOM-6 | PW | 2025-02-18 | 2025-02-21 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-02-17 | OSD30 | DV116.11 | Routine | 10-3-066 | Building 10 | COATING SOLUTION PREP.-4 | PW | 2025-02-18 | 2025-02-21 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-02-17 | OSD31 | DV116.10 | Routine | 10-3-065 | Building 10 | COATING SOLUTION PREP.-3 | PW | 2025-02-18 | 2025-02-21 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-02-17 | OSD32 | SV116.07 | Routine | 10-3-064 | Building 10 | COATING ROOM-5 | PW | 2025-02-18 | 2025-02-21 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-02-17 | OSD33 | SV116.06 | Routine | 10-3-063 | Building 10 | COATING ROOM-4 | PW | 2025-02-18 | 2025-02-21 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-02-17 | OSD36 | DV116.03 | Routine | 10-2-034 | Building 10 | SAMPLE PREPARATION | PW | 2025-02-18 | 2025-02-21 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-02-17 | OSD37 | DV116.06 | Routine | 10-2-034 | Building 10 | SAMPLE PREPARATION | PW | 2025-02-18 | 2025-02-21 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-02-17 | OSD38 | DV116.07 | Routine | 10-2-032 | Building 10 | GLASS-WARE WASHING | PW | 2025-02-18 | 2025-02-21 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-02-17 | OSD39 | DV116.05 | Routine | 10-2-032 | Building 10 | GLASS-WARE WASHING | PW | 2025-02-18 | 2025-02-21 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-02-17 | OSD40 | DV116.04 | Routine | 10-2-037 | Building 10 | SKID FOR BIN WASHING-1 | PW | 2025-02-18 | 2025-02-21 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-02-17 | BU19-14 | SV-14 | Routine | PROCESS WATER (B19) | Building 19 | AFTER RO SYSTEM NO.12 SV14 | PRW | 2025-02-18 | 2025-02-21 | 1 | 0 | 1 | NA | 500 | PASSED | PR
2025-02-17 | OSD34 | SV116.02 | Routine | 10-2-037 | Building 10 | SKID FOR BIN WASHING-2 | PW | 2025-02-18 | 2025-02-21 | 0 | 0 | 0 | with-tube | 100 | PASSED | 10
2025-02-17 | OSD34 | SV116.02 | Routine | 10-2-037 | Building 10 | SKID FOR BIN WASHING-2 | PW | 2025-02-18 | 2025-02-21 | 0 | 0 | 0 | w/o-Tube | 100 | PASSED | 10
2025-02-17 | GOSD03 | V50-61(10) | Routine | WATER SYSTEM (B10) | Building 10 | After Cartridge filter 5 µm (B10) | PRW | 2025-02-18 | 2025-02-21 | 47 | 67 | 57 | NA | 500 | PASSED | WA
2025-02-17 | GOSD04 | V50-11C(10) | Routine | WATER SYSTEM (B10) | Building 10 | After RO (Before EDI) (B10) | RO water | 2025-02-18 | 2025-02-21 | 0 | 0 | 0 | NA | 500 | PASSED | WA
2025-02-17 | GOSD05 | V50-39(10) | Routine | WATER SYSTEM (B10) | Building 10 | After EDI (B10) | PW | 2025-02-18 | 2025-02-21 | 0 | 0 | 0 | NA | 100 | PASSED | WA
2025-02-28 | GOSD02 | V50-60(10) | Routine | WATER SYSTEM (B10) | Building 10 | Before Cartridge filter 5 µm (B10) | PRW | 2025-03-01 | 2025-03-04 | 1 | 1 | 1 | NA | 500 | PASSED | WA
2025-02-28 | GOSD03 | V50-61(10) | Routine | WATER SYSTEM (B10) | Building 10 | After Cartridge filter 5 µm (B10) | PRW | 2025-03-01 | 2025-03-04 | 115 | 82 | 99 | NA | 500 | PASSED | WA
2025-02-28 | OSD43 | DV116.26 | Routine | 10-4-015 | Building 10 | WATER SYSTEM ROOM | PW | 2025-03-01 | 2025-03-04 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-02-28 | OSD01 | SV116.15 | Routine | 10-4-012 | Building 10 | CIP SKID-1 FOR BIN WASHING-1 | PW | 2025-03-01 | 2025-03-04 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-02-28 | OSD02 | SV116.16 | Routine | 10-4-012 | Building 10 | WIP SKID-3 FOR GRANULATION POTENT | PW | 2025-03-01 | 2025-03-04 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-02-28 | OSD03 | SV116.17 | Routine | 10-4-012 | Building 10 | CIP SKID-2 FOR BIN WASHING-1 | PW | 2025-03-01 | 2025-03-04 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-02-28 | OSD04 | SV116.18 | Routine | 10-4-012 | Building 10 | WIP SKID-1 FOR GRANULATION NON POTENT | PW | 2025-03-01 | 2025-03-04 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-02-28 | OSD05 | SV116.19 | Routine | 10-4-012 | Building 10 | WIP SKID-2 FOR GRANULATION NON POTENT | PW | 2025-03-01 | 2025-03-04 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-02-28 | OSD35 | SV116.01 | Routine | 10-2-021 | Building 10 | INSTRUMENT-1 | PW | 2025-03-01 | 2025-03-04 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-02-28 | OSD34 | SV116.02 | Routine | 10-2-037 | Building 10 | SKID FOR BIN WASHING-2 | PW | 2025-03-01 | 2025-03-04 | 0 | 0 | 0 | with-tube | 100 | PASSED | 10
2025-02-28 | OSD34 | SV116.02 | Routine | 10-2-037 | Building 10 | SKID FOR BIN WASHING-2 | PW | 2025-03-01 | 2025-03-04 | 0 | 0 | 0 | w/o-Tube | 100 | PASSED | 10
2025-02-28 | GOSD06 | SV113.01 | Routine | WATER SYSTEM (B10) | Building 10 | After Storage tank (B10) | PW | 2025-03-01 | 2025-03-04 | 0 | 0 | 0 | NA | 100 | PASSED | WA
2025-02-28 | GOSD07 | SV115.02 | Routine | WATER SYSTEM (B10) | Building 10 | After UV (B10) | PW | 2025-03-01 | 2025-03-04 | 0 | 0 | 0 | NA | 100 | PASSED | WA
2025-02-28 | GOSD08 | SV117.01 | Routine | WATER SYSTEM (B10) | Building 10 | Return loop (B10) | PW | 2025-03-01 | 2025-03-04 | 0 | 0 | 0 | NA | 100 | PASSED | WA
2025-03-03 | GOSD01 | VB-05(10) | Routine | WATER SYSTEM (B10) | Building 10 | After Chlorine circulation tank (B10) | PRW | 2025-03-04 | 2025-03-07 | 10 | 7 | 9 | NA | 500 | PASSED | WA
2025-03-03 | GOSD03 | V50-61(10) | Routine | WATER SYSTEM (B10) | Building 10 | After Cartridge filter 5 µm (B10) | PRW | 2025-03-04 | 2025-03-07 | 72 | 74 | 73 | NA | 500 | PASSED | WA
2025-03-03 | OSD27 | DV116.17 | Routine | 10-3-117 | Building 10 | IPQC-2 | PW | 2025-03-04 | 2025-03-07 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-03-03 | OSD09 | DV116.14 | Routine | 10-3-086 | Building 10 | TOOL WASHING | PW | 2025-03-04 | 2025-03-07 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-03-03 | OSD12 | DV116.12 | Routine | 10-3-078 | Building 10 | WASHING | PW | 2025-03-04 | 2025-03-07 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-03-03 | OSD11 | DV116.13 | Routine | 10-3-078 | Building 10 | WASHING | PW | 2025-03-04 | 2025-03-07 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-03-03 | OSD08 | SV116.11 | Routine | 10-3-107 | Building 10 | WET GRANULATION-2 | PW | 2025-03-04 | 2025-03-07 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-03-03 | OSD06 | DV116.18 | Routine | 10-3-111 | Building 10 | WET GRANULATION-5 | PW | 2025-03-04 | 2025-03-07 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-03-03 | OSD07 | DV116.16 | Routine | 10-3-107 | Building 10 | WET GRANULATION-2 | PW | 2025-03-04 | 2025-03-07 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-03-03 | OSD10 | SV116.09 | Routine | 10-3-078 | Building 10 | WASHING | PW | 2025-03-04 | 2025-03-07 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-03-03 | OSD28 | DV116.15 | Routine | 10-3-104 | Building 10 | BINDER PREPARATION | PW | 2025-03-04 | 2025-03-07 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-03-03 | OSD34 | SV116.02 | Routine | 10-2-037 | Building 10 | SKID FOR BIN WASHING-2 | PW | 2025-03-04 | 2025-03-07 | 0 | 0 | 0 | with-tube | 100 | ไม่สายยาง | 10
2025-03-03 | OSD34 | SV116.02 | Routine | 10-2-037 | Building 10 | SKID FOR BIN WASHING-2 | PW | 2025-03-04 | 2025-03-07 | 0 | 0 | 0 | w/o-Tube | 100 | PASSED | 10
2025-03-03 | GOSD04 | V50-11C(10) | Routine | WATER SYSTEM (B10) | Building 10 | After RO (Before EDI) (B10) | RO water | 2025-03-04 | 2025-03-07 | 0 | 0 | 0 | NA | 500 | PASSED | WA
2025-03-03 | GOSD05 | V50-39(10) | Routine | WATER SYSTEM (B10) | Building 10 | After EDI (B10) | PW | 2025-03-04 | 2025-03-07 | 0 | 0 | 0 | NA | 100 | PASSED | WA
2025-03-10 | OSD29 | SV116.08 | Routine | 10-3-067 | Building 10 | COATING ROOM-6 | PW | 2025-03-11 | 2025-03-14 | 2 | 1 | 2 | NA | 100 | PASSED | 10
2025-03-10 | OSD39 | DV116.05 | Routine | 10-2-032 | Building 10 | GLASS-WARE WASHING | PW | 2025-03-11 | 2025-03-14 | 1 | 0 | 1 | NA | 100 | PASSED | 10
2025-03-10 | OSD33 | SV116.06 | Routine | 10-3-063 | Building 10 | COATING ROOM-4 | PW | 2025-03-11 | 2025-03-14 | 39 | 43 | 41 | NA | 100 | PASSED | 10
2025-03-10 | OSD22 | SV116.05 | Routine | 10-3-062 | Building 10 | COATING ROOM-3 | PW | 2025-03-11 | 2025-03-14 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-03-10 | OSD40 | DV116.04 | Routine | 10-2-037 | Building 10 | SKID FOR BIN WASHING-1 | PW | 2025-03-11 | 2025-03-14 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-03-10 | OSD25 | DV116.08 | Routine | 10-3-059 | Building 10 | COATING SOLUTION PREP.-1 | PW | 2025-03-11 | 2025-03-14 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-03-10 | OSD26 | SV116.03 | Routine | 10-3-058 | Building 10 | COATING ROOM-1 | PW | 2025-03-11 | 2025-03-14 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-03-10 | OSD36 | DV116.03 | Routine | 10-2-034 | Building 10 | SAMPLE PREPARATION | PW | 2025-03-11 | 2025-03-14 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-03-10 | OSD37 | DV116.06 | Routine | 10-2-034 | Building 10 | SAMPLE PREPARATION | PW | 2025-03-11 | 2025-03-14 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-03-10 | OSD38 | DV116.07 | Routine | 10-2-032 | Building 10 | GLASS-WARE WASHING | PW | 2025-03-11 | 2025-03-14 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-03-10 | OSD31 | DV116.10 | Routine | 10-3-065 | Building 10 | COATING SOLUTION PREP.-3 | PW | 2025-03-11 | 2025-03-14 | 1 | 1 | 1 | NA | 100 | PASSED | 10
2025-03-10 | OSD30 | DV116.11 | Routine | 10-3-066 | Building 10 | COATING SOLUTION PREP.-4 | PW | 2025-03-11 | 2025-03-14 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-03-10 | OSD24 | DV116.09 | Routine | 10-3-060 | Building 10 | COATING SOLUTION PREP.-2 | PW | 2025-03-11 | 2025-03-14 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-03-10 | OSD32 | SV116.07 | Routine | 10-3-064 | Building 10 | COATING ROOM-5 | PW | 2025-03-11 | 2025-03-14 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-03-10 | OSD23 | SV116.04 | Routine | 10-3-061 | Building 10 | COATING ROOM-2 | PW | 2025-03-11 | 2025-03-14 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-03-10 | OSD34 | SV116.02 | Routine | 10-2-037 | Building 10 | SKID FOR BIN WASHING-2 | PW | 2025-03-11 | 2025-03-14 | 0 | 0 | 0 | with-tube | 100 | PASSED | 10
2025-03-10 | OSD34 | SV116.02 | Routine | 10-2-037 | Building 10 | SKID FOR BIN WASHING-2 | PW | 2025-03-11 | 2025-03-14 | 0 | 0 | 0 | w/o-Tube | 100 | PASSED | 10
2025-03-10 | GOSD06 | SV113.01 | Routine | WATER SYSTEM (B10) | Building 10 | After Storage tank (B10) | PW | 2025-03-11 | 2025-03-14 | 0 | 0 | 0 | NA | 100 | PASSED | WA
2025-03-10 | GOSD07 | SV115.02 | Routine | WATER SYSTEM (B10) | Building 10 | After UV (B10) | PW | 2025-03-11 | 2025-03-14 | 0 | 0 | 0 | NA | 100 | PASSED | WA
2025-03-10 | GOSD08 | SV117.01 | Routine | WATER SYSTEM (B10) | Building 10 | Return loop (B10) | PW | 2025-03-11 | 2025-03-14 | 0 | 0 | 0 | NA | 100 | PASSED | WA
2025-03-21 | GOSD01 | VB-05(10) | Routine | WATER SYSTEM (B10) | Building 10 | After Chlorine circulation tank (B10) | PRW | 2025-03-22 | 2025-03-25 | 0 | 0 | 0 | NA | 500 | PASSED | WA
2025-03-21 | GOSD03 | V50-61(10) | Routine | WATER SYSTEM (B10) | Building 10 | After Cartridge filter 5 µm (B10) | PRW | 2025-03-22 | 2025-03-25 | 475 | 433 | 454 | NA | 500 | PASSED | WA
2025-03-21 | OSD34 | SV116.02 | Routine | 10-2-037 | Building 10 | SKID FOR BIN WASHING-2 | PW | 2025-03-22 | 2025-03-25 | 0 | 0 | 0 | with-tube | 100 | PASSED | 10
2025-03-21 | OSD34 | SV116.02 | Routine | 10-2-037 | Building 10 | SKID FOR BIN WASHING-2 | PW | 2025-03-22 | 2025-03-25 | 0 | 0 | 0 | w/o-Tube | 100 | PASSED | 10
2025-03-21 | OSD21 | SV116.12 | Routine | 10-3-144 | Building 10 | COATING-P | PW | 2025-03-22 | 2025-03-25 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-03-21 | OSD18 | SV116.13 | Routine | 10-3-152 | Building 10 | WASHING-P | PW | 2025-03-22 | 2025-03-25 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-03-21 | OSD42 | DV116.01 | Routine | 10-1-057 | Building 10 | WASHING-P | PW | 2025-03-22 | 2025-03-25 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-03-21 | OSD41 | DV116.02 | Routine | 10-1-115 | Building 10 | WASHING | PW | 2025-03-22 | 2025-03-25 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-03-21 | OSD20 | DV116.19 | Routine | 10-3-143 | Building 10 | COATING SOLUTION PREP.-P | PW | 2025-03-22 | 2025-03-25 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-03-21 | OSD19 | DV116.20 | Routine | 10-3-149 | Building 10 | IPQC-1-P | PW | 2025-03-22 | 2025-03-25 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-03-21 | OSD16 | DV116.21 | Routine | 10-3-152 | Building 10 | WASHING-P | PW | 2025-03-22 | 2025-03-25 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-03-21 | OSD17 | DV116.22 | Routine | 10-3-152 | Building 10 | WASHING-P | PW | 2025-03-22 | 2025-03-25 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-03-21 | OSD15 | DV116.23 | Routine | 10-3-159 | Building 10 | BINDER PREPARATION-P | PW | 2025-03-22 | 2025-03-25 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-03-21 | OSD14 | DV116.24 | Routine | 10-3-163 | Building 10 | WET GRANULATION 1-P | PW | 2025-03-22 | 2025-03-25 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-03-21 | OSD13 | DV116.25 | Routine | 10-3-171 | Building 10 | TOOL WASHING-P | PW | 2025-03-22 | 2025-03-25 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-03-21 | BU19-14 | SV-14 | Routine | PROCESS WATER (B19) | Building 19 | AFTER RO SYSTEM NO.12 SV14 | PRW | 2025-03-22 | 2025-03-25 | 0 | 0 | 0 | NA | 500 | PASSED | PR
2025-03-21 | GOSD04 | V50-11C(10) | Routine | WATER SYSTEM (B10) | Building 10 | After RO (Before EDI) (B10) | RO water | 2025-03-22 | 2025-03-25 | 0 | 0 | 0 | NA | 500 | PASSED | WA
2025-03-21 | GOSD05 | V50-39(10) | Routine | WATER SYSTEM (B10) | Building 10 | After EDI (B10) | PW | 2025-03-22 | 2025-03-25 | 0 | 0 | 0 | NA | 100 | PASSED | WA
2025-04-04 | GOSD01 | VB-05(10) | Routine | WATER SYSTEM (B10) | Building 10 | After Chlorine circulation tank (B10) | PRW | 2025-04-05 | 2025-04-08 | 0 | 0 | 0 | NA | 500 | PASSED | WA
2025-04-04 | GOSD03 | V50-61(10) | Routine | WATER SYSTEM (B10) | Building 10 | After Cartridge filter 5 µm (B10) | PRW | 2025-04-05 | 2025-04-08 | 493 | 508 | 501 | NA | 500 | NOT-PASSED | WA
2025-04-04 | OSD35 | SV116.01 | Routine | 10-2-021 | Building 10 | INSTRUMENT-1 | PW | 2025-04-05 | 2025-04-08 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-04-04 | OSD34 | SV116.02 | Routine | 10-2-037 | Building 10 | SKID FOR BIN WASHING-2 | PW | 2025-04-05 | 2025-04-08 | 0 | 0 | 0 | with-tube | 100 | PASSED | 10
2025-04-04 | OSD34 | SV116.02 | Routine | 10-2-037 | Building 10 | SKID FOR BIN WASHING-2 | PW | 2025-04-05 | 2025-04-08 | 0 | 0 | 0 | w/o-Tube | 100 | PASSED | 10
2025-04-04 | OSD10 | SV116.09 | Routine | 10-3-078 | Building 10 | WASHING | PW | 2025-04-05 | 2025-04-08 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-04-04 | OSD08 | SV116.11 | Routine | 10-3-107 | Building 10 | WET GRANULATION-2 | PW | 2025-04-05 | 2025-04-08 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-04-04 | OSD01 | SV116.15 | Routine | 10-4-012 | Building 10 | CIP SKID-1 FOR BIN WASHING-1 | PW | 2025-04-05 | 2025-04-08 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-04-04 | OSD02 | SV116.16 | Routine | 10-4-012 | Building 10 | WIP SKID-3 FOR GRANULATION POTENT | PW | 2025-04-05 | 2025-04-08 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-04-04 | OSD03 | SV116.17 | Routine | 10-4-012 | Building 10 | CIP SKID-2 FOR BIN WASHING-1 | PW | 2025-04-05 | 2025-04-08 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-04-04 | OSD04 | SV116.18 | Routine | 10-4-012 | Building 10 | WIP SKID-1 FOR GRANULATION NON POTENT | PW | 2025-04-05 | 2025-04-08 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-04-04 | OSD05 | SV116.19 | Routine | 10-4-012 | Building 10 | WIP SKID-2 FOR GRANULATION NON POTENT | PW | 2025-04-05 | 2025-04-08 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-04-04 | OSD12 | DV116.12 | Routine | 10-3-078 | Building 10 | WASHING | PW | 2025-04-05 | 2025-04-08 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-04-04 | OSD11 | DV116.13 | Routine | 10-3-078 | Building 10 | WASHING | PW | 2025-04-05 | 2025-04-08 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-04-04 | OSD09 | DV116.14 | Routine | 10-3-086 | Building 10 | TOOL WASHING | PW | 2025-04-05 | 2025-04-08 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-04-04 | OSD28 | DV116.15 | Routine | 10-3-104 | Building 10 | BINDER PREPARATION | PW | 2025-04-05 | 2025-04-08 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-04-04 | OSD07 | DV116.16 | Routine | 10-3-107 | Building 10 | WET GRANULATION-2 | PW | 2025-04-05 | 2025-04-08 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-04-04 | OSD27 | DV116.17 | Routine | 10-3-117 | Building 10 | IPQC-2 | PW | 2025-04-05 | 2025-04-08 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-04-04 | OSD06 | DV116.18 | Routine | 10-3-111 | Building 10 | WET GRANULATION-5 | PW | 2025-04-05 | 2025-04-08 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-04-04 | OSD43 | DV116.26 | Routine | 10-4-015 | Building 10 | WATER SYSTEM ROOM | PW | 2025-04-05 | 2025-04-08 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-04-04 | GOSD04 | V50-11C(10) | Routine | WATER SYSTEM (B10) | Building 10 | After RO (Before EDI) (B10) | RO water | 2025-04-05 | 2025-04-08 | 0 | 0 | 0 | NA | 500 | PASSED | WA
2025-04-04 | GOSD05 | V50-39(10) | Routine | WATER SYSTEM (B10) | Building 10 | After EDI (B10) | PW | 2025-04-05 | 2025-04-08 | 0 | 0 | 0 | NA | 100 | PASSED | WA
2025-04-04 | GOSD06 | SV113.01 | Routine | WATER SYSTEM (B10) | Building 10 | After Storage tank (B10) | PW | 2025-04-05 | 2025-04-08 | 0 | 0 | 0 | NA | 100 | PASSED | WA
2025-04-04 | GOSD07 | SV115.02 | Routine | WATER SYSTEM (B10) | Building 10 | After UV (B10) | PW | 2025-04-05 | 2025-04-08 | 0 | 0 | 0 | NA | 100 | PASSED | WA
2025-04-04 | GOSD08 | SV117.01 | Routine | WATER SYSTEM (B10) | Building 10 | Return loop (B10) | PW | 2025-04-05 | 2025-04-08 | 0 | 0 | 0 | NA | 100 | PASSED | WA
2025-04-11 | OSD25 | DV116.08 | Routine | 10-3-059 | Building 10 | COATING SOLUTION PREP.-1 | PW | 2025-04-12 | 2025-04-15 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-04-11 | OSD24 | DV116.09 | Routine | 10-3-060 | Building 10 | COATING SOLUTION PREP.-2 | PW | 2025-04-12 | 2025-04-15 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-04-11 | OSD31 | DV116.10 | Routine | 10-3-065 | Building 10 | COATING SOLUTION PREP.-3 | PW | 2025-04-12 | 2025-04-15 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-04-11 | OSD31 | DV116.10 | Routine | 10-3-065 | Building 10 | COATING SOLUTION PREP.-3 | PW | 2025-04-12 | 2025-04-15 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-04-11 | OSD37 | DV116.06 | Routine | 10-2-034 | Building 10 | SAMPLE PREPARATION | PW | 2025-04-12 | 2025-04-15 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-04-11 | OSD38 | DV116.07 | Routine | 10-2-032 | Building 10 | GLASS-WARE WASHING | PW | 2025-04-12 | 2025-04-15 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-04-11 | OSD40 | DV116.04 | Routine | 10-2-037 | Building 10 | SKID FOR BIN WASHING-1 | PW | 2025-04-12 | 2025-04-15 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-04-11 | OSD39 | DV116.05 | Routine | 10-2-032 | Building 10 | GLASS-WARE WASHING | PW | 2025-04-12 | 2025-04-15 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-04-11 | OSD36 | DV116.03 | Routine | 10-2-034 | Building 10 | SAMPLE PREPARATION | PW | 2025-04-12 | 2025-04-15 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-04-11 | OSD33 | SV116.06 | Routine | 10-3-063 | Building 10 | COATING ROOM-4 | PW | 2025-04-12 | 2025-04-15 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-04-11 | OSD32 | SV116.07 | Routine | 10-3-064 | Building 10 | COATING ROOM-5 | PW | 2025-04-12 | 2025-04-15 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-04-11 | OSD22 | SV116.05 | Routine | 10-3-062 | Building 10 | COATING ROOM-3 | PW | 2025-04-12 | 2025-04-15 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-04-11 | OSD29 | SV116.08 | Routine | 10-3-067 | Building 10 | COATING ROOM-6 | PW | 2025-04-12 | 2025-04-15 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-04-11 | OSD26 | SV116.03 | Routine | 10-3-058 | Building 10 | COATING ROOM-1 | PW | 2025-04-12 | 2025-04-15 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-04-11 | OSD23 | SV116.04 | Routine | 10-3-061 | Building 10 | COATING ROOM-2 | PW | 2025-04-12 | 2025-04-15 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-04-11 | OSD34 | SV116.02 | Routine | 10-2-037 | Building 10 | SKID FOR BIN WASHING-2 | PW | 2025-04-12 | 2025-04-15 | 0 | 0 | 0 | with-tube | 100 | PASSED | 10
2025-04-11 | OSD34 | SV116.02 | Routine | 10-2-037 | Building 10 | SKID FOR BIN WASHING-2 | PW | 2025-04-12 | 2025-04-15 | 0 | 0 | 0 | w/o-Tube | 100 | PASSED | 10
2025-04-11 | OSD30 | DV116.11 | Routine | 10-3-066 | Building 10 | COATING SOLUTION PREP.-4 | PW | 2025-04-12 | 2025-04-15 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-04-11 | GOSD06 | SV113.01 | Routine | WATER SYSTEM (B10) | Building 10 | After Storage tank (B10) | PW | 2025-04-12 | 2025-04-15 | 0 | 0 | 0 | NA | 100 | PASSED | WA
2025-04-11 | GOSD07 | SV115.02 | Routine | WATER SYSTEM (B10) | Building 10 | After UV (B10) | PW | 2025-04-12 | 2025-04-15 | 0 | 0 | 0 | NA | 100 | PASSED | WA
2025-04-11 | GOSD08 | SV117.01 | Routine | WATER SYSTEM (B10) | Building 10 | Return loop (B10) | PW | 2025-04-12 | 2025-04-15 | 0 | 0 | 0 | NA | 100 | PASSED | WA
2025-04-22 | OSD42 | DV116.01 | Routine | 10-1-057 | Building 10 | WASHING-P | PW | 2025-04-23 | 2025-04-26 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-04-22 | OSD41 | DV116.02 | Routine | 10-1-115 | Building 10 | WASHING | PW | 2025-04-23 | 2025-04-26 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-04-22 | OSD13 | DV116.25 | Routine | 10-3-171 | Building 10 | TOOL WASHING-P | PW | 2025-04-23 | 2025-04-26 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-04-22 | OSD14 | DV116.24 | Routine | 10-3-163 | Building 10 | WET GRANULATION 1-P | PW | 2025-04-23 | 2025-04-26 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-04-22 | OSD15 | DV116.23 | Routine | 10-3-159 | Building 10 | BINDER PREPARATION-P | PW | 2025-04-23 | 2025-04-26 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-04-22 | OSD16 | DV116.21 | Routine | 10-3-152 | Building 10 | WASHING-P | PW | 2025-04-23 | 2025-04-26 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-04-22 | OSD17 | DV116.22 | Routine | 10-3-152 | Building 10 | WASHING-P | PW | 2025-04-23 | 2025-04-26 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-04-22 | OSD18 | SV116.13 | Routine | 10-3-152 | Building 10 | WASHING-P | PW | 2025-04-23 | 2025-04-26 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-04-22 | OSD19 | DV116.20 | Routine | 10-3-149 | Building 10 | IPQC-1-P | PW | 2025-04-23 | 2025-04-26 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-04-22 | OSD20 | DV116.19 | Routine | 10-3-143 | Building 10 | COATING SOLUTION PREP.-P | PW | 2025-04-23 | 2025-04-26 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-04-22 | OSD21 | SV116.12 | Routine | 10-3-144 | Building 10 | COATING-P | PW | 2025-04-23 | 2025-04-26 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-04-22 | BU19-14 | SV-14 | Routine | PROCESS WATER (B19) | Building 19 | AFTER RO SYSTEM NO.12 SV14 | PRW | 2025-04-23 | 2025-04-26 | 0 | 0 | 0 | NA | 500 | PASSED | PR
2025-04-29 | GOSD01 | VB-05(10) | Routine | WATER SYSTEM (B10) | Building 10 | After Chlorine circulation tank (B10) | PRW | 2025-04-30 | 2025-05-03 | 0 | 0 | 0 | NA | 500 | PASSED | WA
2025-04-29 | GOSD03 | V50-61(10) | Routine | WATER SYSTEM (B10) | Building 10 | After Cartridge filter 5 µm (B10) | PRW | 2025-04-30 | 2025-05-03 | 999 | 999 | 999 | NA | 500 | NOT-PASSED | WA
2025-04-29 | GOSD04 | V50-11C(10) | Routine | WATER SYSTEM (B10) | Building 10 | After RO (Before EDI) (B10) | RO water | 2025-04-30 | 2025-05-03 | 0 | 0 | 0 | NA | 500 | PASSED | WA
2025-04-29 | OSD01 | SV116.15 | Routine | 10-4-012 | Building 10 | CIP SKID-1 FOR BIN WASHING-1 | PW | 2025-04-30 | 2025-05-03 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-04-29 | OSD02 | SV116.16 | Routine | 10-4-012 | Building 10 | WIP SKID-3 FOR GRANULATION POTENT | PW | 2025-04-30 | 2025-05-03 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-04-29 | OSD03 | SV116.17 | Routine | 10-4-012 | Building 10 | CIP SKID-2 FOR BIN WASHING-1 | PW | 2025-04-30 | 2025-05-03 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-04-29 | OSD04 | SV116.18 | Routine | 10-4-012 | Building 10 | WIP SKID-1 FOR GRANULATION NON POTENT | PW | 2025-04-30 | 2025-05-03 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-04-29 | OSD05 | SV116.19 | Routine | 10-4-012 | Building 10 | WIP SKID-2 FOR GRANULATION NON POTENT | PW | 2025-04-30 | 2025-05-03 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-04-29 | OSD34 | SV116.02 | Routine | 10-2-037 | Building 10 | SKID FOR BIN WASHING-2 | PW | 2025-04-30 | 2025-05-03 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-04-29 | OSD35 | SV116.01 | Routine | 10-2-021 | Building 10 | INSTRUMENT-1 | PW | 2025-04-30 | 2025-05-03 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-04-29 | OSD43 | DV116.26 | Routine | 10-4-015 | Building 10 | WATER SYSTEM ROOM | PW | 2025-04-30 | 2025-05-03 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-04-29 | GOSD05 | V50-39(10) | Routine | WATER SYSTEM (B10) | Building 10 | After EDI (B10) | PW | 2025-04-30 | 2025-05-03 | 0 | 0 | 0 | NA | 100 | PASSED | WA
2025-04-29 | GOSD06 | SV113.01 | Routine | WATER SYSTEM (B10) | Building 10 | After Storage tank (B10) | PW | 2025-04-30 | 2025-05-03 | 0 | 0 | 0 | NA | 100 | PASSED | WA
2025-04-29 | GOSD07 | SV115.02 | Routine | WATER SYSTEM (B10) | Building 10 | After UV (B10) | PW | 2025-04-30 | 2025-05-03 | 0 | 0 | 0 | NA | 100 | PASSED | WA
2025-04-29 | GOSD08 | SV117.01 | Routine | WATER SYSTEM (B10) | Building 10 | Return loop (B10) | PW | 2025-04-30 | 2025-05-03 | 0 | 0 | 0 | NA | 100 | PASSED | WA
2025-05-16 | GOSD01 | VB-05(10) | Routine | WATER SYSTEM (B10) | Building 10 | After Chlorine circulation tank (B10) | PRW | 2025-05-17 | 2025-05-20 | 24 | 36 | 30 | NA | 500 | PASSED | WA
2025-05-16 | GOSD03 | V50-61(10) | Routine | WATER SYSTEM (B10) | Building 10 | After Cartridge filter 5 µm (B10) | PRW | 2025-05-17 | 2025-05-20 | 999 | 999 | 999 | NA | 500 | NOT-PASSED | WA
2025-05-16 | GOSD04 | V50-11C(10) | Routine | WATER SYSTEM (B10) | Building 10 | After RO (Before EDI) (B10) | RO water | 2025-05-17 | 2025-05-20 | 0 | 0 | 0 | NA | 500 | PASSED | WA
2025-05-16 | OSD13 | DV116.25 | Routine | 10-3-171 | Building 10 | TOOL WASHING-P | PW | 2025-05-17 | 2025-05-20 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-05-16 | OSD20 | DV116.19 | Routine | 10-3-143 | Building 10 | COATING SOLUTION PREP.-P | PW | 2025-05-17 | 2025-05-20 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-05-16 | OSD19 | DV116.20 | Routine | 10-3-149 | Building 10 | IPQC-1-P | PW | 2025-05-17 | 2025-05-20 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-05-16 | OSD21 | SV116.12 | Routine | 10-3-144 | Building 10 | COATING-P | PW | 2025-05-17 | 2025-05-20 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-05-16 | OSD18 | SV116.13 | Routine | 10-3-152 | Building 10 | WASHING-P | PW | 2025-05-17 | 2025-05-20 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-05-16 | OSD35 | SV116.01 | Routine | 10-2-021 | Building 10 | INSTRUMENT-1 | PW | 2025-05-17 | 2025-05-20 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-05-16 | OSD41 | DV116.02 | Routine | 10-1-115 | Building 10 | WASHING | PW | 2025-05-17 | 2025-05-20 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-05-16 | OSD16 | DV116.21 | Routine | 10-3-152 | Building 10 | WASHING-P | PW | 2025-05-17 | 2025-05-20 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-05-16 | OSD17 | DV116.22 | Routine | 10-3-152 | Building 10 | WASHING-P | PW | 2025-05-17 | 2025-05-20 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-05-16 | OSD15 | DV116.23 | Routine | 10-3-159 | Building 10 | BINDER PREPARATION-P | PW | 2025-05-17 | 2025-05-20 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-05-16 | OSD14 | DV116.24 | Routine | 10-3-163 | Building 10 | WET GRANULATION 1-P | PW | 2025-05-17 | 2025-05-20 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-05-16 | OSD42 | DV116.01 | Routine | 10-1-057 | Building 10 | WASHING-P | PW | 2025-05-17 | 2025-05-20 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-05-16 | GOSD05 | V50-39(10) | Routine | WATER SYSTEM (B10) | Building 10 | After EDI (B10) | PW | 2025-05-17 | 2025-05-20 | 0 | 0 | 0 | NA | 100 | PASSED | WA
2025-05-16 | GOSD06 | SV113.01 | Routine | WATER SYSTEM (B10) | Building 10 | After Storage tank (B10) | PW | 2025-05-17 | 2025-05-20 | 0 | 0 | 0 | NA | 100 | PASSED | WA
2025-05-16 | GOSD07 | SV115.02 | Routine | WATER SYSTEM (B10) | Building 10 | After UV (B10) | PW | 2025-05-17 | 2025-05-20 | 0 | 0 | 0 | NA | 100 | PASSED | WA
2025-05-16 | GOSD08 | SV117.01 | Routine | WATER SYSTEM (B10) | Building 10 | Return loop (B10) | PW | 2025-05-17 | 2025-05-20 | 0 | 0 | 0 | NA | 100 | PASSED | WA
2025-05-19 | OSD23 | SV116.04 | Routine | 10-3-061 | Building 10 | COATING ROOM-2 | PW | 2025-05-20 | 2025-05-23 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-05-19 | OSD36 | DV116.03 | Routine | 10-2-034 | Building 10 | SAMPLE PREPARATION | PW | 2025-05-20 | 2025-05-23 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-05-19 | OSD10 | SV116.09 | Routine | 10-3-078 | Building 10 | WASHING | PW | 2025-05-20 | 2025-05-23 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-05-19 | OSD37 | DV116.06 | Routine | 10-2-034 | Building 10 | SAMPLE PREPARATION | PW | 2025-05-20 | 2025-05-23 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-05-19 | OSD38 | DV116.07 | Routine | 10-2-032 | Building 10 | GLASS-WARE WASHING | PW | 2025-05-20 | 2025-05-23 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-05-19 | OSD40 | DV116.04 | Routine | 10-2-037 | Building 10 | SKID FOR BIN WASHING-1 | PW | 2025-05-20 | 2025-05-23 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-05-19 | OSD39 | DV116.05 | Routine | 10-2-032 | Building 10 | GLASS-WARE WASHING | PW | 2025-05-20 | 2025-05-23 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-05-19 | OSD25 | DV116.08 | Routine | 10-3-059 | Building 10 | COATING SOLUTION PREP.-1 | PW | 2025-05-20 | 2025-05-23 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-05-19 | OSD26 | SV116.03 | Routine | 10-3-058 | Building 10 | COATING ROOM-1 | PW | 2025-05-20 | 2025-05-23 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-05-19 | OSD31 | DV116.10 | Routine | 10-3-065 | Building 10 | COATING SOLUTION PREP.-3 | PW | 2025-05-20 | 2025-05-23 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-05-19 | OSD30 | DV116.11 | Routine | 10-3-066 | Building 10 | COATING SOLUTION PREP.-4 | PW | 2025-05-20 | 2025-05-23 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-05-19 | OSD08 | SV116.11 | Routine | 10-3-107 | Building 10 | WET GRANULATION-2 | PW | 2025-05-20 | 2025-05-23 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-05-19 | OSD12 | DV116.12 | Routine | 10-3-078 | Building 10 | WASHING | PW | 2025-05-20 | 2025-05-23 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-05-19 | OSD07 | DV116.16 | Routine | 10-3-107 | Building 10 | WET GRANULATION-2 | PW | 2025-05-20 | 2025-05-23 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-05-19 | OSD11 | DV116.13 | Routine | 10-3-078 | Building 10 | WASHING | PW | 2025-05-20 | 2025-05-23 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-05-19 | OSD32 | SV116.07 | Routine | 10-3-064 | Building 10 | COATING ROOM-5 | PW | 2025-05-20 | 2025-05-23 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-05-19 | OSD29 | SV116.08 | Routine | 10-3-067 | Building 10 | COATING ROOM-6 | PW | 2025-05-20 | 2025-05-23 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-05-19 | OSD22 | SV116.05 | Routine | 10-3-062 | Building 10 | COATING ROOM-3 | PW | 2025-05-20 | 2025-05-23 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-05-19 | OSD33 | SV116.06 | Routine | 10-3-063 | Building 10 | COATING ROOM-4 | PW | 2025-05-20 | 2025-05-23 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-05-19 | OSD27 | DV116.17 | Routine | 10-3-117 | Building 10 | IPQC-2 | PW | 2025-05-20 | 2025-05-23 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-05-19 | OSD06 | DV116.18 | Routine | 10-3-111 | Building 10 | WET GRANULATION-5 | PW | 2025-05-20 | 2025-05-23 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-05-19 | OSD09 | DV116.14 | Routine | 10-3-086 | Building 10 | TOOL WASHING | PW | 2025-05-20 | 2025-05-23 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-05-19 | OSD28 | DV116.15 | Routine | 10-3-104 | Building 10 | BINDER PREPARATION | PW | 2025-05-20 | 2025-05-23 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-05-19 | OSD24 | DV116.09 | Routine | 10-3-060 | Building 10 | COATING SOLUTION PREP.-2 | PW | 2025-05-20 | 2025-05-23 | 79 | 97 | 88 | NA | 100 | PASSED | 10
2025-06-06 | GOSD01 | VB-05(10) | Routine | WATER SYSTEM (B10) | Building 10 | After Chlorine circulation tank (B10) | PRW | 2025-06-07 | 2025-06-10 | 17 | 18 | 18 | NA | 500 | PASSED | WA
2025-06-06 | GOSD03 | V50-61(10) | Routine | WATER SYSTEM (B10) | Building 10 | After Cartridge filter 5 µm (B10) | PRW | 2025-06-07 | 2025-06-10 | 534 | 626 | 580 | NA | 500 | NOT-PASSED | WA
2025-06-06 | GOSD04 | V50-11C(10) | Routine | WATER SYSTEM (B10) | Building 10 | After RO (Before EDI) (B10) | RO water | 2025-06-07 | 2025-06-10 | 0 | 0 | 0 | NA | 500 | PASSED | WA
2025-06-06 | OSD35 | SV116.01 | Routine | 10-2-021 | Building 10 | INSTRUMENT-1 | PW | 2025-06-07 | 2025-06-10 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-06-06 | OSD34 | SV116.02 | Routine | 10-2-037 | Building 10 | SKID FOR BIN WASHING-2 | PW | 2025-06-07 | 2025-06-10 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-06-06 | OSD43 | DV116.26 | Routine | 10-4-015 | Building 10 | WATER SYSTEM ROOM | PW | 2025-06-07 | 2025-06-10 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-06-06 | OSD03 | SV116.17 | Routine | 10-4-012 | Building 10 | CIP SKID-2 FOR BIN WASHING-1 | PW | 2025-06-07 | 2025-06-10 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-06-06 | OSD04 | SV116.18 | Routine | 10-4-012 | Building 10 | WIP SKID-1 FOR GRANULATION NON POTENT | PW | 2025-06-07 | 2025-06-10 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-06-06 | OSD02 | SV116.16 | Routine | 10-4-012 | Building 10 | WIP SKID-3 FOR GRANULATION POTENT | PW | 2025-06-07 | 2025-06-10 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-06-06 | OSD01 | SV116.15 | Routine | 10-4-012 | Building 10 | CIP SKID-1 FOR BIN WASHING-1 | PW | 2025-06-07 | 2025-06-10 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-06-06 | OSD05 | SV116.19 | Routine | 10-4-012 | Building 10 | WIP SKID-2 FOR GRANULATION NON POTENT | PW | 2025-06-07 | 2025-06-10 | 34 | 40 | 37 | NA | 100 | PASSED | 10
2025-06-06 | BU19-14 | SV-14 | Routine | PROCESS WATER (B19) | Building 19 | AFTER RO SYSTEM NO.12 SV14 | PRW | 2025-06-07 | 2025-06-10 | 867 | 760 | 814 | NA | 500 | NOT-PASSED | PR
2025-06-06 | GOSD05 | V50-39(10) | Routine | WATER SYSTEM (B10) | Building 10 | After EDI (B10) | PW | 2025-06-07 | 2025-06-10 | 0 | 0 | 0 | NA | 100 | PASSED | WA
2025-06-06 | GOSD06 | SV113.01 | Routine | WATER SYSTEM (B10) | Building 10 | After Storage tank (B10) | PW | 2025-06-07 | 2025-06-10 | 4 | 1 | 3 | NA | 100 | PASSED | WA
2025-06-06 | GOSD07 | SV115.02 | Routine | WATER SYSTEM (B10) | Building 10 | After UV (B10) | PW | 2025-06-07 | 2025-06-10 | 0 | 0 | 0 | NA | 100 | PASSED | WA
2025-06-06 | GOSD08 | SV117.01 | Routine | WATER SYSTEM (B10) | Building 10 | Return loop (B10) | PW | 2025-06-07 | 2025-06-10 | 0 | 0 | 0 | NA | 100 | PASSED | WA
2025-06-11 | GOSD01 | VB-05(10) | Routine | WATER SYSTEM (B10) | Building 10 | After Chlorine circulation tank (B10) | PRW | 2025-06-12 | 2025-06-15 | 4 | 4 | 4 | NA | 500 | PASSED | WA
2025-06-11 | GOSD03 | V50-61(10) | Routine | WATER SYSTEM (B10) | Building 10 | After Cartridge filter 5 µm (B10) | PRW | 2025-06-12 | 2025-06-15 | 960 | 823 | 892 | NA | 500 | NOT-PASSED | WA
2025-06-11 | GOSD04 | V50-11C(10) | Routine | WATER SYSTEM (B10) | Building 10 | After RO (Before EDI) (B10) | RO water | 2025-06-12 | 2025-06-15 | 0 | 0 | 0 | NA | 500 | PASSED | WA
2025-06-11 | OSD12 | DV116.12 | Routine | 10-3-078 | Building 10 | WASHING | PW | 2025-06-12 | 2025-06-15 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-06-11 | OSD10 | SV116.09 | Routine | 10-3-078 | Building 10 | WASHING | PW | 2025-06-12 | 2025-06-15 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-06-11 | OSD08 | SV116.11 | Routine | 10-3-107 | Building 10 | WET GRANULATION-2 | PW | 2025-06-12 | 2025-06-15 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-06-11 | OSD27 | DV116.17 | Routine | 10-3-117 | Building 10 | IPQC-2 | PW | 2025-06-12 | 2025-06-15 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-06-11 | OSD06 | DV116.18 | Routine | 10-3-111 | Building 10 | WET GRANULATION-5 | PW | 2025-06-12 | 2025-06-15 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-06-11 | OSD07 | DV116.16 | Routine | 10-3-107 | Building 10 | WET GRANULATION-2 | PW | 2025-06-12 | 2025-06-15 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-06-11 | OSD28 | DV116.15 | Routine | 10-3-104 | Building 10 | BINDER PREPARATION | PW | 2025-06-12 | 2025-06-15 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-06-11 | OSD11 | DV116.13 | Routine | 10-3-078 | Building 10 | WASHING | PW | 2025-06-12 | 2025-06-15 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-06-11 | OSD09 | DV116.14 | Routine | 10-3-086 | Building 10 | TOOL WASHING | PW | 2025-06-12 | 2025-06-15 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-06-11 | GOSD05 | V50-39(10) | Routine | WATER SYSTEM (B10) | Building 10 | After EDI (B10) | PW | 2025-06-12 | 2025-06-15 | 0 | 0 | 0 | NA | 100 | PASSED | WA
2025-06-17 | OSD36 | DV116.03 | Routine | 10-2-034 | Building 10 | SAMPLE PREPARATION | PW | 2025-06-18 | 2025-06-21 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-06-17 | OSD40 | DV116.04 | Routine | 10-2-037 | Building 10 | SKID FOR BIN WASHING-1 | PW | 2025-06-18 | 2025-06-21 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-06-17 | OSD39 | DV116.05 | Routine | 10-2-032 | Building 10 | GLASS-WARE WASHING | PW | 2025-06-18 | 2025-06-21 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-06-17 | OSD37 | DV116.06 | Routine | 10-2-034 | Building 10 | SAMPLE PREPARATION | PW | 2025-06-18 | 2025-06-21 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-06-17 | OSD38 | DV116.07 | Routine | 10-2-032 | Building 10 | GLASS-WARE WASHING | PW | 2025-06-18 | 2025-06-21 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-06-17 | OSD25 | DV116.08 | Routine | 10-3-059 | Building 10 | COATING SOLUTION PREP.-1 | PW | 2025-06-18 | 2025-06-21 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-06-17 | OSD24 | DV116.09 | Routine | 10-3-060 | Building 10 | COATING SOLUTION PREP.-2 | PW | 2025-06-18 | 2025-06-21 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-06-17 | OSD31 | DV116.10 | Routine | 10-3-065 | Building 10 | COATING SOLUTION PREP.-3 | PW | 2025-06-18 | 2025-06-21 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-06-17 | OSD30 | DV116.11 | Routine | 10-3-066 | Building 10 | COATING SOLUTION PREP.-4 | PW | 2025-06-18 | 2025-06-21 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-06-17 | OSD26 | SV116.03 | Routine | 10-3-058 | Building 10 | COATING ROOM-1 | PW | 2025-06-18 | 2025-06-21 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-06-17 | OSD23 | SV116.04 | Routine | 10-3-061 | Building 10 | COATING ROOM-2 | PW | 2025-06-18 | 2025-06-21 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-06-17 | OSD22 | SV116.05 | Routine | 10-3-062 | Building 10 | COATING ROOM-3 | PW | 2025-06-18 | 2025-06-21 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-06-17 | OSD33 | SV116.06 | Routine | 10-3-063 | Building 10 | COATING ROOM-4 | PW | 2025-06-18 | 2025-06-21 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-06-17 | OSD32 | SV116.07 | Routine | 10-3-064 | Building 10 | COATING ROOM-5 | PW | 2025-06-18 | 2025-06-21 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-06-17 | OSD29 | SV116.08 | Routine | 10-3-067 | Building 10 | COATING ROOM-6 | PW | 2025-06-18 | 2025-06-21 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-06-17 | GOSD06 | SV113.01 | Routine | WATER SYSTEM (B10) | Building 10 | After Storage tank (B10) | PW | 2025-06-18 | 2025-06-21 | 0 | 0 | 0 | NA | 100 | PASSED | WA
2025-06-17 | GOSD07 | SV115.02 | Routine | WATER SYSTEM (B10) | Building 10 | After UV (B10) | PW | 2025-06-18 | 2025-06-21 | 0 | 0 | 0 | NA | 100 | PASSED | WA
2025-06-17 | GOSD08 | SV117.01 | Routine | WATER SYSTEM (B10) | Building 10 | Return loop (B10) | PW | 2025-06-18 | 2025-06-21 | 0 | 0 | 0 | NA | 100 | PASSED | WA
2025-06-23 | GOSD01 | VB-05(10) | Routine | WATER SYSTEM (B10) | Building 10 | After Chlorine circulation tank (B10) | PRW | 2025-06-24 | 2025-06-27 | 35 | 25 | 30 | NA | 500 | PASSED | WA
2025-06-23 | GOSD03 | V50-61(10) | Routine | WATER SYSTEM (B10) | Building 10 | After Cartridge filter 5 µm (B10) | PRW | 2025-06-24 | 2025-06-27 | 999 | 999 | 999 | NA | 500 | NOT-PASSED | WA
2025-06-23 | GOSD04 | V50-11C(10) | Routine | WATER SYSTEM (B10) | Building 10 | After RO (Before EDI) (B10) | RO water | 2025-06-24 | 2025-06-27 | 0 | 0 | 0 | NA | 500 | PASSED | WA
2025-06-23 | OSD17 | DV116.22 | Routine | 10-3-152 | Building 10 | WASHING-P | PW | 2025-06-24 | 2025-06-27 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-06-23 | OSD18 | SV116.13 | Routine | 10-3-152 | Building 10 | WASHING-P | PW | 2025-06-24 | 2025-06-27 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-06-23 | OSD15 | DV116.23 | Routine | 10-3-159 | Building 10 | BINDER PREPARATION-P | PW | 2025-06-24 | 2025-06-27 | 7 | 5 | 6 | NA | 100 | PASSED | 10
2025-06-23 | OSD41 | DV116.02 | Routine | 10-1-115 | Building 10 | WASHING | PW | 2025-06-24 | 2025-06-27 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-06-23 | OSD21 | SV116.12 | Routine | 10-3-144 | Building 10 | COATING-P | PW | 2025-06-24 | 2025-06-27 | 3 | 0 | 2 | NA | 100 | PASSED | 10
2025-06-23 | OSD14 | DV116.24 | Routine | 10-3-163 | Building 10 | WET GRANULATION 1-P | PW | 2025-06-24 | 2025-06-27 | 3 | 7 | 5 | NA | 100 | PASSED | 10
2025-06-23 | OSD19 | DV116.20 | Routine | 10-3-149 | Building 10 | IPQC-1-P | PW | 2025-06-24 | 2025-06-27 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-06-23 | OSD16 | DV116.21 | Routine | 10-3-152 | Building 10 | WASHING-P | PW | 2025-06-24 | 2025-06-27 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-06-23 | OSD13 | DV116.25 | Routine | 10-3-171 | Building 10 | TOOL WASHING-P | PW | 2025-06-24 | 2025-06-27 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-06-23 | OSD20 | DV116.19 | Routine | 10-3-143 | Building 10 | COATING SOLUTION PREP.-P | PW | 2025-06-24 | 2025-06-27 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-06-23 | OSD42 | DV116.01 | Routine | 10-1-057 | Building 10 | WASHING-P | PW | 2025-06-24 | 2025-06-27 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-06-23 | GOSD05 | V50-39(10) | Routine | WATER SYSTEM (B10) | Building 10 | After EDI (B10) | PW | 2025-06-24 | 2025-06-27 | 0 | 0 | 0 | NA | 100 | PASSED | WA
2025-06-27 | OSD43 | DV116.26 | Routine | 10-4-015 | Building 10 | WATER SYSTEM ROOM | PW | 2025-06-28 | 2025-07-01 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-06-27 | OSD35 | SV116.01 | Routine | 10-2-021 | Building 10 | INSTRUMENT-1 | PW | 2025-06-28 | 2025-07-01 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-06-27 | OSD05 | SV116.19 | Routine | 10-4-012 | Building 10 | WIP SKID-2 FOR GRANULATION NON POTENT | PW | 2025-06-28 | 2025-07-01 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-06-27 | OSD43 | DV116.26 | Routine | 10-4-015 | Building 10 | WATER SYSTEM ROOM | PW | 2025-06-28 | 2025-07-01 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-06-27 | OSD03 | SV116.17 | Routine | 10-4-012 | Building 10 | CIP SKID-2 FOR BIN WASHING-1 | PW | 2025-06-28 | 2025-07-01 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-06-27 | OSD04 | SV116.18 | Routine | 10-4-012 | Building 10 | WIP SKID-1 FOR GRANULATION NON POTENT | PW | 2025-06-28 | 2025-07-01 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-06-27 | OSD01 | SV116.15 | Routine | 10-4-012 | Building 10 | CIP SKID-1 FOR BIN WASHING-1 | PW | 2025-06-28 | 2025-07-01 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-06-27 | OSD02 | SV116.16 | Routine | 10-4-012 | Building 10 | WIP SKID-3 FOR GRANULATION POTENT | PW | 2025-06-28 | 2025-07-01 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-06-27 | OSD34 | SV116.02 | Routine | 10-2-037 | Building 10 | SKID FOR BIN WASHING-2 | PW | 2025-06-28 | 2025-07-01 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-06-27 | BU19-14 | SV-14 | Routine | PROCESS WATER (B19) | Building 19 | AFTER RO SYSTEM NO.12 SV14 | PRW | 2025-06-28 | 2025-07-01 | 0 | 0 | 0 | NA | 500 | PASSED | PR
2025-06-27 | GOSD06 | SV113.01 | Routine | WATER SYSTEM (B10) | Building 10 | After Storage tank (B10) | PW | 2025-06-28 | 2025-07-01 | 0 | 0 | 0 | NA | 100 | PASSED | WA
2025-06-27 | GOSD07 | SV115.02 | Routine | WATER SYSTEM (B10) | Building 10 | After UV (B10) | PW | 2025-06-28 | 2025-07-01 | 0 | 0 | 0 | NA | 100 | PASSED | WA
2025-06-27 | GOSD08 | SV117.01 | Routine | WATER SYSTEM (B10) | Building 10 | Return loop (B10) | PW | 2025-06-28 | 2025-07-01 | 0 | 0 | 0 | NA | 100 | PASSED | WA
2025-07-07 | GOSD01 | VB-05(10) | Routine | WATER SYSTEM (B10) | Building 10 | After Chlorine circulation tank (B10) | PRW | 2025-07-08 | 2025-07-11 | 0 | 0 | 0 | NA | 500 | PASSED | WA
2025-07-07 | GOSD03 | V50-61(10) | Routine | WATER SYSTEM (B10) | Building 10 | After Cartridge filter 5 µm (B10) | PRW | 2025-07-08 | 2025-07-11 | 999 | 999 | 999 | NA | 500 | NOT-PASSED | WA
2025-07-07 | GOSD04 | V50-11C(10) | Routine | WATER SYSTEM (B10) | Building 10 | After RO (Before EDI) (B10) | RO water | 2025-07-08 | 2025-07-11 | 0 | 0 | 0 | NA | 500 | PASSED | WA
2025-07-07 | GOSD05 | V50-39(10) | Routine | WATER SYSTEM (B10) | Building 10 | After EDI (B10) | PW | 2025-07-08 | 2025-07-11 | 0 | 0 | 0 | NA | 100 | PASSED | WA
2025-07-07 | BU19-15 | SV-15 | Routine | PROCESS WATER (B19) | Building 19 | AFTER RO SYSTEM NO.12 SV15 | PRW | 2025-07-08 | 2025-07-11 | 169 | 213 | 191 | NA | 500 | PASSED | PR
2025-07-07 | BU19-14 | SV-14 | Routine | PROCESS WATER (B19) | Building 19 | AFTER RO SYSTEM NO.12 SV14 | PRW | 2025-07-08 | 2025-07-11 | 664 | 541 | 603 | NA | 500 | NOT-PASSED | PR
2025-07-07 | OSD10 | SV116.09 | Routine | 10-3-078 | Building 10 | WASHING | PW | 2025-07-08 | 2025-07-11 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-07-07 | OSD08 | SV116.11 | Routine | 10-3-107 | Building 10 | WET GRANULATION-2 | PW | 2025-07-08 | 2025-07-11 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-07-07 | OSD12 | DV116.12 | Routine | 10-3-078 | Building 10 | WASHING | PW | 2025-07-08 | 2025-07-11 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-07-07 | OSD11 | DV116.13 | Routine | 10-3-078 | Building 10 | WASHING | PW | 2025-07-08 | 2025-07-11 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-07-07 | OSD09 | DV116.14 | Routine | 10-3-086 | Building 10 | TOOL WASHING | PW | 2025-07-08 | 2025-07-11 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-07-07 | OSD28 | DV116.15 | Routine | 10-3-104 | Building 10 | BINDER PREPARATION | PW | 2025-07-08 | 2025-07-11 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-07-07 | OSD07 | DV116.16 | Routine | 10-3-107 | Building 10 | WET GRANULATION-2 | PW | 2025-07-08 | 2025-07-11 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-07-07 | OSD27 | DV116.17 | Routine | 10-3-117 | Building 10 | IPQC-2 | PW | 2025-07-08 | 2025-07-11 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-07-07 | OSD06 | DV116.18 | Routine | 10-3-111 | Building 10 | WET GRANULATION-5 | PW | 2025-07-08 | 2025-07-11 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-07-14 | GOSD01 | VB-05(10) | Routine | WATER SYSTEM (B10) | Building 10 | After Chlorine circulation tank (B10) | PRW | 2025-07-15 | 2025-07-18 | 23 | 21 | 22 | NA | 500 | PASSED | WA
2025-07-14 | GOSD03 | V50-61(10) | Routine | WATER SYSTEM (B10) | Building 10 | After Cartridge filter 5 µm (B10) | PRW | 2025-07-15 | 2025-07-18 | 999 | 999 | 999 | NA | 500 | NOT-PASSED | WA
2025-07-14 | GOSD04 | V50-11C(10) | Routine | WATER SYSTEM (B10) | Building 10 | After RO (Before EDI) (B10) | RO water | 2025-07-15 | 2025-07-18 | 0 | 0 | 0 | NA | 500 | PASSED | WA
2025-07-14 | GOSD05 | V50-39(10) | Routine | WATER SYSTEM (B10) | Building 10 | After EDI (B10) | PW | 2025-07-15 | 2025-07-18 | 0 | 0 | 0 | NA | 100 | PASSED | WA
2025-07-14 | OSD31 | DV116.10 | Routine | 10-3-065 | Building 10 | COATING SOLUTION PREP.-3 | PW | 2025-07-15 | 2025-07-18 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-07-14 | OSD30 | DV116.11 | Routine | 10-3-066 | Building 10 | COATING SOLUTION PREP.-4 | PW | 2025-07-15 | 2025-07-18 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-07-14 | OSD33 | SV116.06 | Routine | 10-3-063 | Building 10 | COATING ROOM-4 | PW | 2025-07-15 | 2025-07-18 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-07-14 | OSD29 | SV116.08 | Routine | 10-3-067 | Building 10 | COATING ROOM-6 | PW | 2025-07-15 | 2025-07-18 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-07-14 | OSD39 | DV116.05 | Routine | 10-2-032 | Building 10 | GLASS-WARE WASHING | PW | 2025-07-15 | 2025-07-18 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-07-14 | OSD37 | DV116.06 | Routine | 10-2-034 | Building 10 | SAMPLE PREPARATION | PW | 2025-07-15 | 2025-07-18 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-07-14 | OSD26 | SV116.03 | Routine | 10-3-058 | Building 10 | COATING ROOM-1 | PW | 2025-07-15 | 2025-07-18 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-07-14 | OSD32 | SV116.07 | Routine | 10-3-064 | Building 10 | COATING ROOM-5 | PW | 2025-07-15 | 2025-07-18 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-07-14 | OSD23 | SV116.04 | Routine | 10-3-061 | Building 10 | COATING ROOM-2 | PW | 2025-07-15 | 2025-07-18 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-07-14 | OSD22 | SV116.05 | Routine | 10-3-062 | Building 10 | COATING ROOM-3 | PW | 2025-07-15 | 2025-07-18 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-07-14 | OSD38 | DV116.07 | Routine | 10-2-032 | Building 10 | GLASS-WARE WASHING | PW | 2025-07-15 | 2025-07-18 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-07-14 | OSD24 | DV116.09 | Routine | 10-3-060 | Building 10 | COATING SOLUTION PREP.-2 | PW | 2025-07-15 | 2025-07-18 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-07-14 | OSD36 | DV116.03 | Routine | 10-2-034 | Building 10 | SAMPLE PREPARATION | PW | 2025-07-15 | 2025-07-18 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-07-14 | OSD40 | DV116.04 | Routine | 10-2-037 | Building 10 | SKID FOR BIN WASHING-1 | PW | 2025-07-15 | 2025-07-18 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-07-14 | OSD25 | DV116.08 | Routine | 10-3-059 | Building 10 | COATING SOLUTION PREP.-1 | PW | 2025-07-15 | 2025-07-18 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-07-14 | GOSD06 | SV113.01 | Routine | WATER SYSTEM (B10) | Building 10 | After Storage tank (B10) | PW | 2025-07-15 | 2025-07-18 | 0 | 0 | 0 | NA | 100 | PASSED | WA
2025-07-14 | GOSD07 | SV115.02 | Routine | WATER SYSTEM (B10) | Building 10 | After UV (B10) | PW | 2025-07-15 | 2025-07-18 | 0 | 0 | 0 | NA | 100 | PASSED | WA
2025-07-14 | GOSD08 | SV117.01 | Routine | WATER SYSTEM (B10) | Building 10 | Return loop (B10) | PW | 2025-07-15 | 2025-07-18 | 0 | 0 | 0 | NA | 100 | PASSED | WA
2025-07-21 | GOCL01 | VB-05 (16) | Routine | WATER SYSTEM (B16) | Building 16 | After Chlorine circulation tank (B16) | PRW | 2025-07-22 | 2025-07-25 | 2 | 3 | 3 | NA | 500 | PASSED | WA
2025-07-21 | GOSD03 | V50-61(10) | Routine | WATER SYSTEM (B10) | Building 10 | After Cartridge filter 5 µm (B10) | PRW | 2025-07-22 | 2025-07-25 | 2 | 0 | 1 | NA | 500 | PASSED | WA
2025-07-21 | GOSD04 | V50-11C(10) | Routine | WATER SYSTEM (B10) | Building 10 | After RO (Before EDI) (B10) | RO water | 2025-07-22 | 2025-07-25 | 1 | 0 | 1 | NA | 500 | PASSED | WA
2025-07-21 | BU19-14 | SV-14 | Routine | PROCESS WATER (B19) | Building 19 | AFTER RO SYSTEM NO.12 SV14 | PRW | 2025-07-22 | 2025-07-25 | 2 | 2 | 2 | NA | 500 | PASSED | PR
2025-07-21 | BU19-15 | SV-15 | Routine | PROCESS WATER (B19) | Building 19 | AFTER RO SYSTEM NO.12 SV15 | PRW | 2025-07-22 | 2025-07-25 | 1 | 4 | 3 | NA | 500 | PASSED | PR
2025-07-21 | OSD21 | SV116.12 | Routine | 10-3-144 | Building 10 | COATING-P | PW | 2025-07-22 | 2025-07-25 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-07-21 | OSD18 | SV116.13 | Routine | 10-3-152 | Building 10 | WASHING-P | PW | 2025-07-22 | 2025-07-25 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-07-21 | OSD16 | DV116.21 | Routine | 10-3-152 | Building 10 | WASHING-P | PW | 2025-07-22 | 2025-07-25 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-07-21 | OSD20 | DV116.19 | Routine | 10-3-143 | Building 10 | COATING SOLUTION PREP.-P | PW | 2025-07-22 | 2025-07-25 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-07-21 | OSD19 | DV116.20 | Routine | 10-3-149 | Building 10 | IPQC-1-P | PW | 2025-07-22 | 2025-07-25 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-07-21 | OSD14 | DV116.24 | Routine | 10-3-163 | Building 10 | WET GRANULATION 1-P | PW | 2025-07-22 | 2025-07-25 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-07-21 | OSD13 | DV116.25 | Routine | 10-3-171 | Building 10 | TOOL WASHING-P | PW | 2025-07-22 | 2025-07-25 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-07-21 | OSD17 | DV116.22 | Routine | 10-3-152 | Building 10 | WASHING-P | PW | 2025-07-22 | 2025-07-25 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-07-21 | OSD15 | DV116.23 | Routine | 10-3-159 | Building 10 | BINDER PREPARATION-P | PW | 2025-07-22 | 2025-07-25 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-07-29 | OSD42 | DV116.01 | Routine | 10-1-057 | Building 10 | WASHING-P | PW | 2025-07-30 | 2025-08-02 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-07-29 | OSD41 | DV116.02 | Routine | 10-1-115 | Building 10 | WASHING | PW | 2025-07-30 | 2025-08-02 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-07-29 | OSD35 | SV116.01 | Routine | 10-2-021 | Building 10 | INSTRUMENT-1 | PW | 2025-07-30 | 2025-08-02 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-07-29 | OSD34 | SV116.02 | Routine | 10-2-037 | Building 10 | SKID FOR BIN WASHING-2 | PW | 2025-07-30 | 2025-08-02 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-07-29 | OSD01 | SV116.15 | Routine | 10-4-012 | Building 10 | CIP SKID-1 FOR BIN WASHING-1 | PW | 2025-07-30 | 2025-08-02 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-07-29 | OSD02 | SV116.16 | Routine | 10-4-012 | Building 10 | WIP SKID-3 FOR GRANULATION POTENT | PW | 2025-07-30 | 2025-08-02 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-07-29 | OSD03 | SV116.17 | Routine | 10-4-012 | Building 10 | CIP SKID-2 FOR BIN WASHING-1 | PW | 2025-07-30 | 2025-08-02 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-07-29 | OSD04 | SV116.18 | Routine | 10-4-012 | Building 10 | WIP SKID-1 FOR GRANULATION NON POTENT | PW | 2025-07-30 | 2025-08-02 | 1 | 0 | 1 | NA | 100 | PASSED | 10
2025-07-29 | OSD05 | SV116.19 | Routine | 10-4-012 | Building 10 | WIP SKID-2 FOR GRANULATION NON POTENT | PW | 2025-07-30 | 2025-08-02 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-07-29 | OSD43 | DV116.26 | Routine | 10-4-015 | Building 10 | WATER SYSTEM ROOM | PW | 2025-07-30 | 2025-08-02 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-07-29 | GOSD06 | SV113.01 | Routine | WATER SYSTEM (B10) | Building 10 | After Storage tank (B10) | PW | 2025-07-30 | 2025-08-02 | 0 | 0 | 0 | NA | 100 | PASSED | WA
2025-07-29 | GOSD07 | SV115.02 | Routine | WATER SYSTEM (B10) | Building 10 | After UV (B10) | PW | 2025-07-30 | 2025-08-02 | 0 | 0 | 0 | NA | 100 | PASSED | WA
2025-07-29 | GOSD08 | SV117.01 | Routine | WATER SYSTEM (B10) | Building 10 | Return loop (B10) | PW | 2025-07-30 | 2025-08-02 | 0 | 0 | 0 | NA | 100 | PASSED | WA
2025-08-04 | GOSD01 | VB-05(10) | Routine | WATER SYSTEM (B10) | Building 10 | After Chlorine circulation tank (B10) | PRW | 2025-08-05 | 2025-08-08 | 0 | 0 | 0 | NA | 500 | PASSED | WA
2025-08-04 | GOSD03 | V50-61(10) | Routine | WATER SYSTEM (B10) | Building 10 | After Cartridge filter 5 µm (B10) | PRW | 2025-08-05 | 2025-08-08 | 251 | 255 | 253 | NA | 500 | PASSED | WA
2025-08-04 | GOSD04 | V50-11C(10) | Routine | WATER SYSTEM (B10) | Building 10 | After RO (Before EDI) (B10) | RO water | 2025-08-05 | 2025-08-08 | 0 | 0 | 0 | NA | 500 | PASSED | WA
2025-08-04 | GOSD05 | V50-39(10) | Routine | WATER SYSTEM (B10) | Building 10 | After EDI (B10) | PW | 2025-08-05 | 2025-08-08 | 0 | 0 | 0 | NA | 100 | PASSED | WA
2025-08-04 | OSD08 | SV116.11 | Routine | 10-3-107 | Building 10 | WET GRANULATION-2 | PW | 2025-08-05 | 2025-08-08 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-08-04 | OSD12 | DV116.12 | Routine | 10-3-078 | Building 10 | WASHING | PW | 2025-08-05 | 2025-08-08 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-08-04 | OSD11 | DV116.13 | Routine | 10-3-078 | Building 10 | WASHING | PW | 2025-08-05 | 2025-08-08 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-08-04 | OSD09 | DV116.14 | Routine | 10-3-086 | Building 10 | TOOL WASHING | PW | 2025-08-05 | 2025-08-08 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-08-04 | OSD28 | DV116.15 | Routine | 10-3-104 | Building 10 | BINDER PREPARATION | PW | 2025-08-05 | 2025-08-08 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-08-04 | OSD07 | DV116.16 | Routine | 10-3-107 | Building 10 | WET GRANULATION-2 | PW | 2025-08-05 | 2025-08-08 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-08-04 | OSD27 | DV116.17 | Routine | 10-3-117 | Building 10 | IPQC-2 | PW | 2025-08-05 | 2025-08-08 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-08-04 | OSD06 | DV116.18 | Routine | 10-3-111 | Building 10 | WET GRANULATION-5 | PW | 2025-08-05 | 2025-08-08 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-08-04 | OSD10 | SV116.09 | Routine | 10-3-078 | Building 10 | WASHING | PW | 2025-08-05 | 2025-08-08 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-08-04 | BU19-14 | SV-14 | Routine | PROCESS WATER (B19) | Building 19 | AFTER RO SYSTEM NO.12 SV14 | PRW | 2025-08-05 | 2025-08-08 | 999 | 999 | 999 | NA | 500 | NOT-PASSED | PR
2025-08-04 | BU19-15 | SV-15 | Routine | PROCESS WATER (B19) | Building 19 | AFTER RO SYSTEM NO.12 SV15 | PRW | 2025-08-05 | 2025-08-08 | 999 | 999 | 999 | NA | 500 | NOT-PASSED | PR
2025-08-13 | OSD25 | DV116.08 | Routine | 10-3-059 | Building 10 | COATING SOLUTION PREP.-1 | PW | 2025-08-14 | 2025-08-17 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-08-13 | OSD24 | DV116.09 | Routine | 10-3-060 | Building 10 | COATING SOLUTION PREP.-2 | PW | 2025-08-14 | 2025-08-17 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-08-13 | GOSD06 | SV113.01 | Routine | WATER SYSTEM (B10) | Building 10 | After Storage tank (B10) | PW | 2025-08-14 | 2025-08-17 | 0 | 0 | 0 | NA | 100 | PASSED | WA
2025-08-13 | OSD26 | SV116.03 | Routine | 10-3-058 | Building 10 | COATING ROOM-1 | PW | 2025-08-14 | 2025-08-17 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-08-13 | OSD23 | SV116.04 | Routine | 10-3-061 | Building 10 | COATING ROOM-2 | PW | 2025-08-14 | 2025-08-17 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-08-13 | OSD22 | SV116.05 | Routine | 10-3-062 | Building 10 | COATING ROOM-3 | PW | 2025-08-14 | 2025-08-17 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-08-13 | OSD33 | SV116.06 | Routine | 10-3-063 | Building 10 | COATING ROOM-4 | PW | 2025-08-14 | 2025-08-17 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-08-13 | OSD32 | SV116.07 | Routine | 10-3-064 | Building 10 | COATING ROOM-5 | PW | 2025-08-14 | 2025-08-17 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-08-13 | OSD29 | SV116.08 | Routine | 10-3-067 | Building 10 | COATING ROOM-6 | PW | 2025-08-14 | 2025-08-17 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-08-13 | OSD36 | DV116.03 | Routine | 10-2-034 | Building 10 | SAMPLE PREPARATION | PW | 2025-08-14 | 2025-08-17 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-08-13 | OSD40 | DV116.04 | Routine | 10-2-037 | Building 10 | SKID FOR BIN WASHING-1 | PW | 2025-08-14 | 2025-08-17 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-08-13 | OSD39 | DV116.05 | Routine | 10-2-032 | Building 10 | GLASS-WARE WASHING | PW | 2025-08-14 | 2025-08-17 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-08-13 | OSD37 | DV116.06 | Routine | 10-2-034 | Building 10 | SAMPLE PREPARATION | PW | 2025-08-14 | 2025-08-17 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-08-13 | OSD38 | DV116.07 | Routine | 10-2-032 | Building 10 | GLASS-WARE WASHING | PW | 2025-08-14 | 2025-08-17 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-08-13 | OSD31 | DV116.10 | Routine | 10-3-065 | Building 10 | COATING SOLUTION PREP.-3 | PW | 2025-08-14 | 2025-08-17 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-08-13 | OSD30 | DV116.11 | Routine | 10-3-066 | Building 10 | COATING SOLUTION PREP.-4 | PW | 2025-08-14 | 2025-08-17 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-08-13 | GOSD07 | SV115.02 | Routine | WATER SYSTEM (B10) | Building 10 | After UV (B10) | PW | 2025-08-14 | 2025-08-17 | 0 | 0 | 0 | NA | 100 | PASSED | WA
2025-08-13 | GOSD08 | SV117.01 | Routine | WATER SYSTEM (B10) | Building 10 | Return loop (B10) | PW | 2025-08-14 | 2025-08-17 | 0 | 0 | 0 | NA | 100 | PASSED | WA
2025-08-18 | GOSD01 | VB-05(10) | Routine | WATER SYSTEM (B10) | Building 10 | After Chlorine circulation tank (B10) | PRW | 2025-08-19 | 2025-08-22 | 0 | 0 | 0 | NA | 500 | PASSED | WA
2025-08-18 | GOSD03 | V50-61(10) | Routine | WATER SYSTEM (B10) | Building 10 | After Cartridge filter 5 µm (B10) | PRW | 2025-08-19 | 2025-08-22 | 176 | 173 | 175 | NA | 500 | PASSED | WA
2025-08-18 | GOSD04 | V50-11C(10) | Routine | WATER SYSTEM (B10) | Building 10 | After RO (Before EDI) (B10) | RO water | 2025-08-19 | 2025-08-22 | 0 | 0 | 0 | NA | 500 | PASSED | WA
2025-08-18 | GOSD05 | V50-39(10) | Routine | WATER SYSTEM (B10) | Building 10 | After EDI (B10) | PW | 2025-08-19 | 2025-08-22 | 0 | 0 | 0 | NA | 100 | PASSED | WA
2025-08-18 | BU19-15 | SV-15 | Routine | PROCESS WATER (B19) | Building 19 | AFTER RO SYSTEM NO.12 SV15 | PRW | 2025-08-19 | 2025-08-22 | 999 | 999 | 999 | NA | 500 | NOT-PASSED | PR
2025-08-18 | OSD17 | DV116.22 | Routine | 10-3-152 | Building 10 | WASHING-P | PW | 2025-08-19 | 2025-08-22 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-08-18 | OSD15 | DV116.23 | Routine | 10-3-159 | Building 10 | BINDER PREPARATION-P | PW | 2025-08-19 | 2025-08-22 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-08-18 | OSD14 | DV116.24 | Routine | 10-3-163 | Building 10 | WET GRANULATION 1-P | PW | 2025-08-19 | 2025-08-22 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-08-18 | OSD13 | DV116.25 | Routine | 10-3-171 | Building 10 | TOOL WASHING-P | PW | 2025-08-19 | 2025-08-22 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-08-18 | BU19-14 | SV-14 | Routine | PROCESS WATER (B19) | Building 19 | AFTER RO SYSTEM NO.12 SV14 | PRW | 2025-08-19 | 2025-08-22 | 176 | 173 | 175 | NA | 500 | PASSED | PR
2025-08-18 | OSD42 | DV116.01 | Routine | 10-1-057 | Building 10 | WASHING-P | PW | 2025-08-19 | 2025-08-22 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-08-18 | OSD19 | DV116.20 | Routine | 10-3-149 | Building 10 | IPQC-1-P | PW | 2025-08-19 | 2025-08-22 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-08-18 | OSD41 | DV116.02 | Routine | 10-1-115 | Building 10 | WASHING | PW | 2025-08-19 | 2025-08-22 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-08-18 | OSD20 | DV116.19 | Routine | 10-3-143 | Building 10 | COATING SOLUTION PREP.-P | PW | 2025-08-19 | 2025-08-22 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-08-18 | OSD21 | SV116.12 | Routine | 10-3-144 | Building 10 | COATING-P | PW | 2025-08-19 | 2025-08-22 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-08-18 | OSD18 | SV116.13 | Routine | 10-3-152 | Building 10 | WASHING-P | PW | 2025-08-19 | 2025-08-22 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-08-18 | OSD16 | DV116.21 | Routine | 10-3-152 | Building 10 | WASHING-P | PW | 2025-08-19 | 2025-08-22 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-08-25 | GOSD06 | SV113.01 | Routine | WATER SYSTEM (B10) | Building 10 | After Storage tank (B10) | PW | 2025-08-26 | 2025-08-29 | 0 | 0 | 0 | NA | 100 | PASSED | WA
2025-08-25 | OSD34 | SV116.02 | Routine | 10-2-037 | Building 10 | SKID FOR BIN WASHING-2 | PW | 2025-08-26 | 2025-08-29 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-08-25 | OSD35 | SV116.01 | Routine | 10-2-021 | Building 10 | INSTRUMENT-1 | PW | 2025-08-26 | 2025-08-29 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-08-25 | OSD04 | SV116.18 | Routine | 10-4-012 | Building 10 | WIP SKID-1 FOR GRANULATION NON POTENT | PW | 2025-08-26 | 2025-08-29 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-08-25 | OSD03 | SV116.17 | Routine | 10-4-012 | Building 10 | CIP SKID-2 FOR BIN WASHING-1 | PW | 2025-08-26 | 2025-08-29 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-08-25 | OSD02 | SV116.16 | Routine | 10-4-012 | Building 10 | WIP SKID-3 FOR GRANULATION POTENT | PW | 2025-08-26 | 2025-08-29 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-08-25 | OSD01 | SV116.15 | Routine | 10-4-012 | Building 10 | CIP SKID-1 FOR BIN WASHING-1 | PW | 2025-08-26 | 2025-08-29 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-08-25 | OSD43 | DV116.26 | Routine | 10-4-015 | Building 10 | WATER SYSTEM ROOM | PW | 2025-08-26 | 2025-08-29 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-08-25 | OSD05 | SV116.19 | Routine | 10-4-012 | Building 10 | WIP SKID-2 FOR GRANULATION NON POTENT | PW | 2025-08-26 | 2025-08-29 | 3 | 5 | 4 | NA | 100 | PASSED | 10
2025-08-25 | GOSD07 | SV115.02 | Routine | WATER SYSTEM (B10) | Building 10 | After UV (B10) | PW | 2025-08-26 | 2025-08-29 | 0 | 0 | 0 | NA | 100 | PASSED | WA
2025-08-25 | GOSD08 | SV117.01 | Routine | WATER SYSTEM (B10) | Building 10 | Return loop (B10) | PW | 2025-08-26 | 2025-08-29 | 0 | 0 | 0 | NA | 100 | PASSED | WA
2025-09-05 | GOSD01 | VB-05(10) | Routine | WATER SYSTEM (B10) | Building 10 | After Chlorine circulation tank (B10) | PRW | 2025-09-06 | 2025-09-09 | 0 | 0 | 0 | NA | 500 | PASSED | WA
2025-09-05 | GOSD03 | V50-61(10) | Routine | WATER SYSTEM (B10) | Building 10 | After Cartridge filter 5 µm (B10) | PRW | 2025-09-06 | 2025-09-09 | 279 | 295 | 287 | NA | 500 | PASSED | WA
2025-09-05 | GOSD04 | V50-11C(10) | Routine | WATER SYSTEM (B10) | Building 10 | After RO (Before EDI) (B10) | RO water | 2025-09-06 | 2025-09-09 | 0 | 0 | 0 | NA | 500 | PASSED | WA
2025-09-05 | GOSD05 | V50-39(10) | Routine | WATER SYSTEM (B10) | Building 10 | After EDI (B10) | PW | 2025-09-06 | 2025-09-09 | 0 | 0 | 0 | NA | 100 | PASSED | WA
2025-09-05 | OSD06 | DV116.18 | Routine | 10-3-111 | Building 10 | WET GRANULATION-5 | PW | 2025-09-06 | 2025-09-09 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-09-05 | OSD12 | DV116.12 | Routine | 10-3-078 | Building 10 | WASHING | PW | 2025-09-06 | 2025-09-09 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-09-05 | OSD11 | DV116.13 | Routine | 10-3-078 | Building 10 | WASHING | PW | 2025-09-06 | 2025-09-09 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-09-05 | OSD09 | DV116.14 | Routine | 10-3-086 | Building 10 | TOOL WASHING | PW | 2025-09-06 | 2025-09-09 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-09-05 | OSD28 | DV116.15 | Routine | 10-3-104 | Building 10 | BINDER PREPARATION | PW | 2025-09-06 | 2025-09-09 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-09-05 | OSD10 | SV116.09 | Routine | 10-3-078 | Building 10 | WASHING | PW | 2025-09-06 | 2025-09-09 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-09-05 | OSD08 | SV116.11 | Routine | 10-3-107 | Building 10 | WET GRANULATION-2 | PW | 2025-09-06 | 2025-09-09 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-09-05 | OSD07 | DV116.16 | Routine | 10-3-107 | Building 10 | WET GRANULATION-2 | PW | 2025-09-06 | 2025-09-09 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-09-05 | OSD27 | DV116.17 | Routine | 10-3-117 | Building 10 | IPQC-2 | PW | 2025-09-06 | 2025-09-09 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-09-12 | GOSD06 | SV113.01 | Routine | WATER SYSTEM (B10) | Building 10 | After Storage tank (B10) | PW | 2025-09-13 | 2025-09-16 | 0 | 0 | 0 | NA | 100 | PASSED | WA
2025-09-12 | BU19-14 | SV-14 | Routine | PROCESS WATER (B19) | Building 19 | AFTER RO SYSTEM NO.12 SV14 | PRW | 2025-09-13 | 2025-09-16 | 0 | 0 | 0 | NA | 500 | PASSED | PR
2025-09-12 | BU19-15 | SV-15 | Routine | PROCESS WATER (B19) | Building 19 | AFTER RO SYSTEM NO.12 SV15 | PRW | 2025-09-13 | 2025-09-16 | 3 | 1 | 2 | NA | 500 | PASSED | PR
2025-09-12 | OSD36 | DV116.03 | Routine | 10-2-034 | Building 10 | SAMPLE PREPARATION | PW | 2025-09-13 | 2025-09-16 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-09-12 | OSD40 | DV116.04 | Routine | 10-2-037 | Building 10 | SKID FOR BIN WASHING-1 | PW | 2025-09-13 | 2025-09-16 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-09-12 | OSD39 | DV116.05 | Routine | 10-2-032 | Building 10 | GLASS-WARE WASHING | PW | 2025-09-13 | 2025-09-16 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-09-12 | OSD37 | DV116.06 | Routine | 10-2-034 | Building 10 | SAMPLE PREPARATION | PW | 2025-09-13 | 2025-09-16 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-09-12 | OSD38 | DV116.07 | Routine | 10-2-032 | Building 10 | GLASS-WARE WASHING | PW | 2025-09-13 | 2025-09-16 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-09-12 | OSD25 | DV116.08 | Routine | 10-3-059 | Building 10 | COATING SOLUTION PREP.-1 | PW | 2025-09-13 | 2025-09-16 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-09-12 | OSD24 | DV116.09 | Routine | 10-3-060 | Building 10 | COATING SOLUTION PREP.-2 | PW | 2025-09-13 | 2025-09-16 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-09-12 | OSD31 | DV116.10 | Routine | 10-3-065 | Building 10 | COATING SOLUTION PREP.-3 | PW | 2025-09-13 | 2025-09-16 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-09-12 | OSD26 | SV116.03 | Routine | 10-3-058 | Building 10 | COATING ROOM-1 | PW | 2025-09-13 | 2025-09-16 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-09-12 | OSD23 | SV116.04 | Routine | 10-3-061 | Building 10 | COATING ROOM-2 | PW | 2025-09-13 | 2025-09-16 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-09-12 | OSD22 | SV116.05 | Routine | 10-3-062 | Building 10 | COATING ROOM-3 | PW | 2025-09-13 | 2025-09-16 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-09-12 | OSD32 | SV116.07 | Routine | 10-3-064 | Building 10 | COATING ROOM-5 | PW | 2025-09-13 | 2025-09-16 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-09-12 | OSD29 | SV116.08 | Routine | 10-3-067 | Building 10 | COATING ROOM-6 | PW | 2025-09-13 | 2025-09-16 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-09-12 | OSD33 | SV116.06 | Routine | 10-3-063 | Building 10 | COATING ROOM-4 | PW | 2025-09-13 | 2025-09-16 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-09-12 | OSD30 | DV116.11 | Routine | 10-3-066 | Building 10 | COATING SOLUTION PREP.-4 | PW | 2025-09-13 | 2025-09-16 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-09-12 | GOSD07 | SV115.02 | Routine | WATER SYSTEM (B10) | Building 10 | After UV (B10) | PW | 2025-09-13 | 2025-09-16 | 0 | 0 | 0 | NA | 100 | PASSED | WA
2025-09-12 | GOSD08 | SV117.01 | Routine | WATER SYSTEM (B10) | Building 10 | Return loop (B10) | PW | 2025-09-13 | 2025-09-16 | 0 | 0 | 0 | NA | 100 | PASSED | WA
2025-09-16 | GOSD01 | VB-05(10) | Routine | WATER SYSTEM (B10) | Building 10 | After Chlorine circulation tank (B10) | PRW | 2025-09-17 | 2025-09-20 | 0 | 0 | 0 | NA | 500 | PASSED | WA
2025-09-16 | GOSD03 | V50-61(10) | Routine | WATER SYSTEM (B10) | Building 10 | After Cartridge filter 5 µm (B10) | PRW | 2025-09-17 | 2025-09-20 | 3 | 2 | 3 | NA | 500 | PASSED | WA
2025-09-16 | GOSD04 | V50-11C(10) | Routine | WATER SYSTEM (B10) | Building 10 | After RO (Before EDI) (B10) | RO water | 2025-09-17 | 2025-09-20 | 0 | 0 | 0 | NA | 500 | PASSED | WA
2025-09-16 | GOSD05 | V50-39(10) | Routine | WATER SYSTEM (B10) | Building 10 | After EDI (B10) | PW | 2025-09-17 | 2025-09-20 | 0 | 0 | 0 | NA | 100 | PASSED | WA
2025-09-16 | OSD21 | SV116.12 | Routine | 10-3-144 | Building 10 | COATING-P | PW | 2025-09-17 | 2025-09-20 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-09-16 | OSD18 | SV116.13 | Routine | 10-3-152 | Building 10 | WASHING-P | PW | 2025-09-17 | 2025-09-20 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-09-16 | OSD42 | DV116.01 | Routine | 10-1-057 | Building 10 | WASHING-P | PW | 2025-09-17 | 2025-09-20 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-09-16 | OSD41 | DV116.02 | Routine | 10-1-115 | Building 10 | WASHING | PW | 2025-09-17 | 2025-09-20 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-09-16 | OSD20 | DV116.19 | Routine | 10-3-143 | Building 10 | COATING SOLUTION PREP.-P | PW | 2025-09-17 | 2025-09-20 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-09-16 | OSD19 | DV116.20 | Routine | 10-3-149 | Building 10 | IPQC-1-P | PW | 2025-09-17 | 2025-09-20 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-09-16 | OSD15 | DV116.23 | Routine | 10-3-159 | Building 10 | BINDER PREPARATION-P | PW | 2025-09-17 | 2025-09-20 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-09-16 | OSD14 | DV116.24 | Routine | 10-3-163 | Building 10 | WET GRANULATION 1-P | PW | 2025-09-17 | 2025-09-20 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-09-16 | OSD16 | DV116.21 | Routine | 10-3-152 | Building 10 | WASHING-P | PW | 2025-09-17 | 2025-09-20 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-09-16 | OSD17 | DV116.22 | Routine | 10-3-152 | Building 10 | WASHING-P | PW | 2025-09-17 | 2025-09-20 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-09-16 | OSD13 | DV116.25 | Routine | 10-3-171 | Building 10 | TOOL WASHING-P | PW | 2025-09-17 | 2025-09-20 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-09-23 | GOSD06 | SV113.01 | Routine | WATER SYSTEM (B10) | Building 10 | After Storage tank (B10) | PW | 2025-09-24 | 2025-09-27 | 0 | 0 | 0 | NA | 100 | PASSED | WA
2025-09-23 | BU19-14 | SV-14 | Routine | PROCESS WATER (B19) | Building 19 | AFTER RO SYSTEM NO.12 SV14 | PRW | 2025-09-24 | 2025-09-27 | 0 | 0 | 0 | NA | 500 | PASSED | PR
2025-09-23 | BU19-15 | SV-15 | Routine | PROCESS WATER (B19) | Building 19 | AFTER RO SYSTEM NO.12 SV15 | PRW | 2025-09-24 | 2025-09-27 | 0 | 0 | 0 | NA | 500 | PASSED | PR
2025-09-23 | OSD43 | DV116.26 | Routine | 10-4-015 | Building 10 | WATER SYSTEM ROOM | PW | 2025-09-24 | 2025-09-27 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-09-23 | OSD35 | SV116.01 | Routine | 10-2-021 | Building 10 | INSTRUMENT-1 | PW | 2025-09-24 | 2025-09-27 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-09-23 | OSD01 | SV116.15 | Routine | 10-4-012 | Building 10 | CIP SKID-1 FOR BIN WASHING-1 | PW | 2025-09-24 | 2025-09-27 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-09-23 | OSD05 | SV116.19 | Routine | 10-4-012 | Building 10 | WIP SKID-2 FOR GRANULATION NON POTENT | PW | 2025-09-24 | 2025-09-27 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-09-23 | OSD04 | SV116.18 | Routine | 10-4-012 | Building 10 | WIP SKID-1 FOR GRANULATION NON POTENT | PW | 2025-09-24 | 2025-09-27 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-09-23 | OSD34 | SV116.02 | Routine | 10-2-037 | Building 10 | SKID FOR BIN WASHING-2 | PW | 2025-09-24 | 2025-09-27 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-09-23 | OSD02 | SV116.16 | Routine | 10-4-012 | Building 10 | WIP SKID-3 FOR GRANULATION POTENT | PW | 2025-09-24 | 2025-09-27 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-09-23 | OSD03 | SV116.17 | Routine | 10-4-012 | Building 10 | CIP SKID-2 FOR BIN WASHING-1 | PW | 2025-09-24 | 2025-09-27 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-09-23 | GOSD08 | SV117.01 | Routine | WATER SYSTEM (B10) | Building 10 | Return loop (B10) | PW | 2025-09-24 | 2025-09-27 | 0 | 0 | 0 | NA | 100 | PASSED | WA
2025-10-03 | GOSD01 | VB-05(10) | Routine | WATER SYSTEM (B10) | Building 10 | After Chlorine circulation tank (B10) | PRW | 2025-10-04 | 2025-10-07 | 0 | 0 | 0 | NA | 500 | PASSED | WA
2025-10-03 | GOSD03 | V50-61(10) | Routine | WATER SYSTEM (B10) | Building 10 | After Cartridge filter 5 µm (B10) | PRW | 2025-10-04 | 2025-10-07 | 1 | 1 | 1 | NA | 500 | PASSED | WA
2025-10-03 | GOSD04 | V50-11C(10) | Routine | WATER SYSTEM (B10) | Building 10 | After RO (Before EDI) (B10) | RO water | 2025-10-04 | 2025-10-07 | 0 | 0 | 0 | NA | 500 | PASSED | WA
2025-10-03 | GOSD05 | V50-39(10) | Routine | WATER SYSTEM (B10) | Building 10 | After EDI (B10) | PW | 2025-10-04 | 2025-10-07 | 0 | 0 | 0 | NA | 100 | PASSED | WA
2025-10-03 | OSD08 | SV116.11 | Routine | 10-3-107 | Building 10 | WET GRANULATION-2 | PW | 2025-10-04 | 2025-10-07 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-10-03 | OSD12 | DV116.12 | Routine | 10-3-078 | Building 10 | WASHING | PW | 2025-10-04 | 2025-10-07 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-10-03 | OSD11 | DV116.13 | Routine | 10-3-078 | Building 10 | WASHING | PW | 2025-10-04 | 2025-10-07 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-10-03 | OSD09 | DV116.14 | Routine | 10-3-086 | Building 10 | TOOL WASHING | PW | 2025-10-04 | 2025-10-07 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-10-03 | OSD28 | DV116.15 | Routine | 10-3-104 | Building 10 | BINDER PREPARATION | PW | 2025-10-04 | 2025-10-07 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-10-03 | OSD07 | DV116.16 | Routine | 10-3-107 | Building 10 | WET GRANULATION-2 | PW | 2025-10-04 | 2025-10-07 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-10-03 | OSD27 | DV116.17 | Routine | 10-3-117 | Building 10 | IPQC-2 | PW | 2025-10-04 | 2025-10-07 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-10-03 | OSD06 | DV116.18 | Routine | 10-3-111 | Building 10 | WET GRANULATION-5 | PW | 2025-10-04 | 2025-10-07 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-10-03 | OSD10 | SV116.09 | Routine | 10-3-078 | Building 10 | WASHING | PW | 2025-10-04 | 2025-10-07 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-10-03 | BU19-14 | SV-14 | Routine | PROCESS WATER (B19) | Building 19 | AFTER RO SYSTEM NO.12 SV14 | PRW | 2025-10-04 | 2025-10-07 | 1 | 1 | 1 | NA | 500 | PASSED | PR
2025-10-03 | BU19-15 | SV-15 | Routine | PROCESS WATER (B19) | Building 19 | AFTER RO SYSTEM NO.12 SV15 | PRW | 2025-10-04 | 2025-10-07 | 1 | 1 | 1 | NA | 500 | PASSED | PR
2025-10-07 | GOSD06 | SV113.01 | Routine | WATER SYSTEM (B10) | Building 10 | After Storage tank (B10) | PW | 2025-10-08 | 2025-10-11 | 0 | 0 | 0 | NA | 100 | PASSED | WA
2025-10-07 | GOSD07 | SV115.02 | Routine | WATER SYSTEM (B10) | Building 10 | After UV (B10) | PW | 2025-10-08 | 2025-10-11 | 0 | 0 | 0 | NA | 100 | PASSED | WA
2025-10-07 | OSD32 | SV116.07 | Routine | 10-3-064 | Building 10 | COATING ROOM-5 | PW | 2025-10-08 | 2025-10-11 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-10-07 | OSD29 | SV116.08 | Routine | 10-3-067 | Building 10 | COATING ROOM-6 | PW | 2025-10-08 | 2025-10-11 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-10-07 | OSD22 | SV116.05 | Routine | 10-3-062 | Building 10 | COATING ROOM-3 | PW | 2025-10-08 | 2025-10-11 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-10-07 | OSD33 | SV116.06 | Routine | 10-3-063 | Building 10 | COATING ROOM-4 | PW | 2025-10-08 | 2025-10-11 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-10-07 | OSD26 | SV116.03 | Routine | 10-3-058 | Building 10 | COATING ROOM-1 | PW | 2025-10-08 | 2025-10-11 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-10-07 | OSD23 | SV116.04 | Routine | 10-3-061 | Building 10 | COATING ROOM-2 | PW | 2025-10-08 | 2025-10-11 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-10-07 | OSD30 | DV116.11 | Routine | 10-3-066 | Building 10 | COATING SOLUTION PREP.-4 | PW | 2025-10-08 | 2025-10-11 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-10-07 | OSD24 | DV116.09 | Routine | 10-3-060 | Building 10 | COATING SOLUTION PREP.-2 | PW | 2025-10-08 | 2025-10-11 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-10-07 | OSD31 | DV116.10 | Routine | 10-3-065 | Building 10 | COATING SOLUTION PREP.-3 | PW | 2025-10-08 | 2025-10-11 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-10-07 | OSD38 | DV116.07 | Routine | 10-2-032 | Building 10 | GLASS-WARE WASHING | PW | 2025-10-08 | 2025-10-11 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-10-07 | OSD25 | DV116.08 | Routine | 10-3-059 | Building 10 | COATING SOLUTION PREP.-1 | PW | 2025-10-08 | 2025-10-11 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-10-07 | OSD39 | DV116.05 | Routine | 10-2-032 | Building 10 | GLASS-WARE WASHING | PW | 2025-10-08 | 2025-10-11 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-10-07 | OSD37 | DV116.06 | Routine | 10-2-034 | Building 10 | SAMPLE PREPARATION | PW | 2025-10-08 | 2025-10-11 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-10-07 | OSD36 | DV116.03 | Routine | 10-2-034 | Building 10 | SAMPLE PREPARATION | PW | 2025-10-08 | 2025-10-11 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-10-07 | OSD40 | DV116.04 | Routine | 10-2-037 | Building 10 | SKID FOR BIN WASHING-1 | PW | 2025-10-08 | 2025-10-11 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-10-07 | GOSD08 | SV117.01 | Routine | WATER SYSTEM (B10) | Building 10 | Return loop (B10) | PW | 2025-10-08 | 2025-10-11 | 0 | 0 | 0 | NA | 100 | PASSED | WA
2025-10-17 | GOSD01 | VB-05(10) | Routine | WATER SYSTEM (B10) | Building 10 | After Chlorine circulation tank (B10) | PRW | 2025-10-18 | 2025-10-21 | 0 | 0 | 0 | NA | 500 | PASSED | WA
2025-10-17 | GOSD03 | V50-61(10) | Routine | WATER SYSTEM (B10) | Building 10 | After Cartridge filter 5 µm (B10) | PRW | 2025-10-18 | 2025-10-21 | 0 | 0 | 0 | NA | 500 | PASSED | WA
2025-10-17 | GOSD04 | V50-11C(10) | Routine | WATER SYSTEM (B10) | Building 10 | After RO (Before EDI) (B10) | RO water | 2025-10-18 | 2025-10-21 | 0 | 0 | 0 | NA | 500 | PASSED | WA
2025-10-17 | GOSD05 | V50-39(10) | Routine | WATER SYSTEM (B10) | Building 10 | After EDI (B10) | PW | 2025-10-18 | 2025-10-21 | 0 | 0 | 0 | NA | 100 | PASSED | WA
2025-10-17 | OSD13 | DV116.25 | Routine | 10-3-171 | Building 10 | TOOL WASHING-P | PW | 2025-10-18 | 2025-10-21 | 1 | 0 | 1 | NA | 100 | PASSED | 10
2025-10-17 | OSD15 | DV116.23 | Routine | 10-3-159 | Building 10 | BINDER PREPARATION-P | PW | 2025-10-18 | 2025-10-21 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-10-17 | OSD14 | DV116.24 | Routine | 10-3-163 | Building 10 | WET GRANULATION 1-P | PW | 2025-10-18 | 2025-10-21 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-10-17 | OSD16 | DV116.21 | Routine | 10-3-152 | Building 10 | WASHING-P | PW | 2025-10-18 | 2025-10-21 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-10-17 | OSD17 | DV116.22 | Routine | 10-3-152 | Building 10 | WASHING-P | PW | 2025-10-18 | 2025-10-21 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-10-17 | OSD20 | DV116.19 | Routine | 10-3-143 | Building 10 | COATING SOLUTION PREP.-P | PW | 2025-10-18 | 2025-10-21 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-10-17 | OSD19 | DV116.20 | Routine | 10-3-149 | Building 10 | IPQC-1-P | PW | 2025-10-18 | 2025-10-21 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-10-17 | OSD21 | SV116.12 | Routine | 10-3-144 | Building 10 | COATING-P | PW | 2025-10-18 | 2025-10-21 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-10-17 | OSD18 | SV116.13 | Routine | 10-3-152 | Building 10 | WASHING-P | PW | 2025-10-18 | 2025-10-21 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-10-17 | OSD42 | DV116.01 | Routine | 10-1-057 | Building 10 | WASHING-P | PW | 2025-10-18 | 2025-10-21 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-10-17 | OSD41 | DV116.02 | Routine | 10-1-115 | Building 10 | WASHING | PW | 2025-10-18 | 2025-10-21 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-10-21 | GOSD06 | SV113.01 | Routine | WATER SYSTEM (B10) | Building 10 | After Storage tank (B10) | PW | 2025-10-22 | 2025-10-25 | 0 | 0 | 0 | NA | 100 | PASSED | WA
2025-10-21 | GOSD07 | SV115.02 | Routine | WATER SYSTEM (B10) | Building 10 | After UV (B10) | PW | 2025-10-22 | 2025-10-25 | 0 | 0 | 0 | NA | 100 | PASSED | WA
2025-10-21 | OSD03 | SV116.17 | Routine | 10-4-012 | Building 10 | CIP SKID-2 FOR BIN WASHING-1 | PW | 2025-10-22 | 2025-10-25 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-10-21 | OSD04 | SV116.18 | Routine | 10-4-012 | Building 10 | WIP SKID-1 FOR GRANULATION NON POTENT | PW | 2025-10-22 | 2025-10-25 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-10-21 | OSD01 | SV116.15 | Routine | 10-4-012 | Building 10 | CIP SKID-1 FOR BIN WASHING-1 | PW | 2025-10-22 | 2025-10-25 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-10-21 | OSD02 | SV116.16 | Routine | 10-4-012 | Building 10 | WIP SKID-3 FOR GRANULATION POTENT | PW | 2025-10-22 | 2025-10-25 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-10-21 | BU19-14 | SV-14 | Routine | PROCESS WATER (B19) | Building 19 | AFTER RO SYSTEM NO.12 SV14 | PRW | 2025-10-22 | 2025-10-25 | 0 | 0 | 0 | NA | 500 | PASSED | PR
2025-10-21 | BU19-15 | SV-15 | Routine | PROCESS WATER (B19) | Building 19 | AFTER RO SYSTEM NO.12 SV15 | PRW | 2025-10-22 | 2025-10-25 | 0 | 0 | 0 | NA | 500 | PASSED | PR
2025-10-21 | OSD35 | SV116.01 | Routine | 10-2-021 | Building 10 | INSTRUMENT-1 | PW | 2025-10-22 | 2025-10-25 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-10-21 | OSD34 | SV116.02 | Routine | 10-2-037 | Building 10 | SKID FOR BIN WASHING-2 | PW | 2025-10-22 | 2025-10-25 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-10-21 | OSD05 | SV116.19 | Routine | 10-4-012 | Building 10 | WIP SKID-2 FOR GRANULATION NON POTENT | PW | 2025-10-22 | 2025-10-25 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-10-21 | OSD43 | DV116.26 | Routine | 10-4-015 | Building 10 | WATER SYSTEM ROOM | PW | 2025-10-22 | 2025-10-25 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-10-21 | GOSD08 | SV117.01 | Routine | WATER SYSTEM (B10) | Building 10 | Return loop (B10) | PW | 2025-10-22 | 2025-10-25 | 0 | 0 | 0 | NA | 100 | PASSED | WA
2025-11-04 | GOSD01 | VB-05(10) | Routine | WATER SYSTEM (B10) | Building 10 | After Chlorine circulation tank (B10) | PRW | 2025-11-05 | 2025-11-08 | 0 | 0 | 0 | NA | 500 | PASSED | WA
2025-11-04 | GOSD03 | V50-61(10) | Routine | WATER SYSTEM (B10) | Building 10 | After Cartridge filter 5 µm (B10) | PRW | 2025-11-05 | 2025-11-08 | 0 | 0 | 0 | NA | 500 | PASSED | WA
2025-11-04 | GOSD04 | V50-11C(10) | Routine | WATER SYSTEM (B10) | Building 10 | After RO (Before EDI) (B10) | RO water | 2025-11-05 | 2025-11-08 | 0 | 0 | 0 | NA | 500 | PASSED | WA
2025-11-04 | GOSD05 | V50-39(10) | Routine | WATER SYSTEM (B10) | Building 10 | After EDI (B10) | PW | 2025-11-05 | 2025-11-08 | 0 | 0 | 0 | NA | 100 | PASSED | WA
2025-11-04 | OSD10 | SV116.09 | Routine | 10-3-078 | Building 10 | WASHING | PW | 2025-11-05 | 2025-11-08 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-11-04 | OSD08 | SV116.11 | Routine | 10-3-107 | Building 10 | WET GRANULATION-2 | PW | 2025-11-05 | 2025-11-08 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-11-04 | OSD12 | DV116.12 | Routine | 10-3-078 | Building 10 | WASHING | PW | 2025-11-05 | 2025-11-08 | 1 | 0 | 1 | NA | 100 | PASSED | 10
2025-11-04 | OSD11 | DV116.13 | Routine | 10-3-078 | Building 10 | WASHING | PW | 2025-11-05 | 2025-11-08 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-11-04 | OSD09 | DV116.14 | Routine | 10-3-086 | Building 10 | TOOL WASHING | PW | 2025-11-05 | 2025-11-08 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-11-04 | OSD27 | DV116.17 | Routine | 10-3-117 | Building 10 | IPQC-2 | PW | 2025-11-05 | 2025-11-08 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-11-04 | OSD07 | DV116.16 | Routine | 10-3-107 | Building 10 | WET GRANULATION-2 | PW | 2025-11-05 | 2025-11-08 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-11-04 | OSD28 | DV116.15 | Routine | 10-3-104 | Building 10 | BINDER PREPARATION | PW | 2025-11-05 | 2025-11-08 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-11-04 | OSD07 | DV116.16 | Routine | 10-3-107 | Building 10 | WET GRANULATION-2 | PW | 2025-11-05 | 2025-11-08 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-11-04 | BU19-14 | SV-14 | Routine | PROCESS WATER (B19) | Building 19 | AFTER RO SYSTEM NO.12 SV14 | PRW | 2025-11-05 | 2025-11-08 | 175 | 264 | 220 | NA | 500 | PASSED | PR
2025-11-04 | BU19-15 | SV-15 | Routine | PROCESS WATER (B19) | Building 19 | AFTER RO SYSTEM NO.12 SV15 | PRW | 2025-11-05 | 2025-11-08 | 243 | 310 | 277 | NA | 500 | PASSED | PR
2025-11-14 | GOCL05 | SV123.01 | Routine | WATER SYSTEM (B16) | Building 16 | After Storage tank (B16) | PW | 2025-11-15 | 2025-11-18 | 0 | 0 | 0 | NA | 100 | PASSED | WA
2025-11-14 | GOCL08 | SV127.01 | Routine | WATER SYSTEM (B16) | Building 16 | Return loop (B16) | PW | 2025-11-15 | 2025-11-18 | 0 | 0 | 0 | NA | 100 | PASSED | WA
2025-11-14 | GOSD06 | SV113.01 | Routine | WATER SYSTEM (B10) | Building 10 | After Storage tank (B10) | PW | 2025-11-15 | 2025-11-18 | 0 | 0 | 0 | NA | 100 | PASSED | WA
2025-11-14 | GOSD07 | SV115.02 | Routine | WATER SYSTEM (B10) | Building 10 | After UV (B10) | PW | 2025-11-15 | 2025-11-18 | 0 | 0 | 0 | NA | 100 | PASSED | WA
2025-11-14 | OSD31 | DV116.10 | Routine | 10-3-065 | Building 10 | COATING SOLUTION PREP.-3 | PW | 2025-11-15 | 2025-11-18 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-11-14 | OSD39 | DV116.05 | Routine | 10-2-032 | Building 10 | GLASS-WARE WASHING | PW | 2025-11-15 | 2025-11-18 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-11-14 | OSD30 | DV116.11 | Routine | 10-3-066 | Building 10 | COATING SOLUTION PREP.-4 | PW | 2025-11-15 | 2025-11-18 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-11-14 | OSD26 | SV116.03 | Routine | 10-3-058 | Building 10 | COATING ROOM-1 | PW | 2025-11-15 | 2025-11-18 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-11-14 | OSD32 | SV116.07 | Routine | 10-3-064 | Building 10 | COATING ROOM-5 | PW | 2025-11-15 | 2025-11-18 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-11-14 | OSD23 | SV116.04 | Routine | 10-3-061 | Building 10 | COATING ROOM-2 | PW | 2025-11-15 | 2025-11-18 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-11-14 | OSD33 | SV116.06 | Routine | 10-3-063 | Building 10 | COATING ROOM-4 | PW | 2025-11-15 | 2025-11-18 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-11-14 | OSD29 | SV116.08 | Routine | 10-3-067 | Building 10 | COATING ROOM-6 | PW | 2025-11-15 | 2025-11-18 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-11-14 | OSD22 | SV116.05 | Routine | 10-3-062 | Building 10 | COATING ROOM-3 | PW | 2025-11-15 | 2025-11-18 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-11-14 | OSD24 | DV116.09 | Routine | 10-3-060 | Building 10 | COATING SOLUTION PREP.-2 | PW | 2025-11-15 | 2025-11-18 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-11-14 | OSD25 | DV116.08 | Routine | 10-3-059 | Building 10 | COATING SOLUTION PREP.-1 | PW | 2025-11-15 | 2025-11-18 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-11-14 | OSD36 | DV116.03 | Routine | 10-2-034 | Building 10 | SAMPLE PREPARATION | PW | 2025-11-15 | 2025-11-18 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-11-14 | OSD37 | DV116.06 | Routine | 10-2-034 | Building 10 | SAMPLE PREPARATION | PW | 2025-11-15 | 2025-11-18 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-11-14 | OSD40 | DV116.04 | Routine | 10-2-037 | Building 10 | SKID FOR BIN WASHING-1 | PW | 2025-11-15 | 2025-11-18 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-11-14 | OSD38 | DV116.07 | Routine | 10-2-032 | Building 10 | GLASS-WARE WASHING | PW | 2025-11-15 | 2025-11-18 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-11-14 | GOSD08 | SV117.01 | Routine | WATER SYSTEM (B10) | Building 10 | Return loop (B10) | PW | 2025-11-15 | 2025-11-18 | 0 | 0 | 0 | NA | 100 | PASSED | WA
2025-11-21 | GOSD01 | VB-05(10) | Routine | WATER SYSTEM (B10) | Building 10 | After Chlorine circulation tank (B10) | PRW | 2025-11-22 | 2025-11-25 | 0 | 0 | 0 | NA | 500 | PASSED | WA
2025-11-21 | GOSD03 | V50-61(10) | Routine | WATER SYSTEM (B10) | Building 10 | After Cartridge filter 5 µm (B10) | PRW | 2025-11-22 | 2025-11-25 | 0 | 0 | 0 | NA | 500 | PASSED | WA
2025-11-21 | GOSD04 | V50-11C(10) | Routine | WATER SYSTEM (B10) | Building 10 | After RO (Before EDI) (B10) | RO water | 2025-11-22 | 2025-11-25 | 0 | 0 | 0 | NA | 500 | PASSED | WA
2025-11-21 | GOSD05 | V50-39(10) | Routine | WATER SYSTEM (B10) | Building 10 | After EDI (B10) | PW | 2025-11-22 | 2025-11-25 | 0 | 0 | 0 | NA | 100 | PASSED | WA
2025-11-21 | OSD13 | DV116.25 | Routine | 10-3-171 | Building 10 | TOOL WASHING-P | PW | 2025-11-22 | 2025-11-25 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-11-21 | OSD15 | DV116.23 | Routine | 10-3-159 | Building 10 | BINDER PREPARATION-P | PW | 2025-11-22 | 2025-11-25 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-11-21 | OSD14 | DV116.24 | Routine | 10-3-163 | Building 10 | WET GRANULATION 1-P | PW | 2025-11-22 | 2025-11-25 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-11-21 | OSD16 | DV116.21 | Routine | 10-3-152 | Building 10 | WASHING-P | PW | 2025-11-22 | 2025-11-25 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-11-21 | OSD17 | DV116.22 | Routine | 10-3-152 | Building 10 | WASHING-P | PW | 2025-11-22 | 2025-11-25 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-11-21 | OSD20 | DV116.19 | Routine | 10-3-143 | Building 10 | COATING SOLUTION PREP.-P | PW | 2025-11-22 | 2025-11-25 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-11-21 | OSD19 | DV116.20 | Routine | 10-3-149 | Building 10 | IPQC-1-P | PW | 2025-11-22 | 2025-11-25 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-11-21 | OSD21 | SV116.12 | Routine | 10-3-144 | Building 10 | COATING-P | PW | 2025-11-22 | 2025-11-25 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-11-21 | OSD18 | SV116.13 | Routine | 10-3-152 | Building 10 | WASHING-P | PW | 2025-11-22 | 2025-11-25 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-11-21 | BU19-14 | SV-14 | Routine | PROCESS WATER (B19) | Building 19 | AFTER RO SYSTEM NO.12 SV14 | PRW | 2025-11-22 | 2025-11-25 | 0 | 0 | 0 | NA | 500 | PASSED | PR
2025-11-21 | BU19-15 | SV-15 | Routine | PROCESS WATER (B19) | Building 19 | AFTER RO SYSTEM NO.12 SV15 | PRW | 2025-11-22 | 2025-11-25 | 0 | 0 | 0 | NA | 500 | PASSED | PR
2025-11-21 | OSD42 | DV116.01 | Routine | 10-1-057 | Building 10 | WASHING-P | PW | 2025-11-22 | 2025-11-25 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-11-21 | OSD34 | SV116.02 | Routine | 10-2-037 | Building 10 | SKID FOR BIN WASHING-2 | PW | 2025-11-22 | 2025-11-25 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-11-25 | GOSD06 | SV113.01 | Routine | WATER SYSTEM (B10) | Building 10 | After Storage tank (B10) | PW | 2025-11-26 | 2025-11-29 | 0 | 0 | 0 | NA | 100 | PASSED | WA
2025-11-25 | GOSD07 | SV115.02 | Routine | WATER SYSTEM (B10) | Building 10 | After UV (B10) | PW | 2025-11-26 | 2025-11-29 | 0 | 0 | 0 | NA | 100 | PASSED | WA
2025-11-25 | GOSD08 | SV117.01 | Routine | WATER SYSTEM (B10) | Building 10 | Return loop (B10) | PW | 2025-11-26 | 2025-11-29 | 0 | 0 | 0 | NA | 100 | PASSED | WA
2025-11-25 | OSD01 | SV116.15 | Routine | 10-4-012 | Building 10 | CIP SKID-1 FOR BIN WASHING-1 | PW | 2025-11-26 | 2025-11-29 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-11-25 | OSD02 | SV116.16 | Routine | 10-4-012 | Building 10 | WIP SKID-3 FOR GRANULATION POTENT | PW | 2025-11-26 | 2025-11-29 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-11-25 | OSD03 | SV116.17 | Routine | 10-4-012 | Building 10 | CIP SKID-2 FOR BIN WASHING-1 | PW | 2025-11-26 | 2025-11-29 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-11-25 | OSD04 | SV116.18 | Routine | 10-4-012 | Building 10 | WIP SKID-1 FOR GRANULATION NON POTENT | PW | 2025-11-26 | 2025-11-29 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-11-25 | OSD05 | SV116.19 | Routine | 10-4-012 | Building 10 | WIP SKID-2 FOR GRANULATION NON POTENT | PW | 2025-11-26 | 2025-11-29 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-11-25 | OSD34 | SV116.02 | Routine | 10-2-037 | Building 10 | SKID FOR BIN WASHING-2 | PW | 2025-11-26 | 2025-11-29 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-11-25 | OSD35 | SV116.01 | Routine | 10-2-021 | Building 10 | INSTRUMENT-1 | PW | 2025-11-26 | 2025-11-29 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-11-25 | OSD43 | DV116.26 | Routine | 10-4-015 | Building 10 | WATER SYSTEM ROOM | PW | 2025-11-26 | 2025-11-29 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-12-02 | BU19-14 | SV-14 | Routine | PROCESS WATER (B19) | Building 19 | AFTER RO SYSTEM NO.12 SV14 | PRW | 2025-12-03 | 2025-12-06 | 0 | 0 | 0 | NA | 500 | PASSED | PR
2025-12-02 | GOSD01 | VB-05(10) | Routine | WATER SYSTEM (B10) | Building 10 | After Chlorine circulation tank (B10) | PRW | 2025-12-03 | 2025-12-06 | 0 | 0 | 0 | NA | 500 | PASSED | WA
2025-12-02 | GOSD02 | V50-60(10) | Routine | WATER SYSTEM (B10) | Building 10 | Before Cartridge filter 5 µm (B10) | PRW | 2025-12-03 | 2025-12-06 | 0 | 0 | 0 | NA | 500 | PASSED | WA
2025-12-02 | GOSD03 | V50-61(10) | Routine | WATER SYSTEM (B10) | Building 10 | After Cartridge filter 5 µm (B10) | PRW | 2025-12-03 | 2025-12-06 | 0 | 0 | 0 | NA | 500 | PASSED | WA
2025-12-02 | GOSD04 | V50-11C(10) | Routine | WATER SYSTEM (B10) | Building 10 | After RO (Before EDI) (B10) | RO water | 2025-12-03 | 2025-12-06 | 0 | 0 | 0 | NA | 100 | PASSED | WA
2025-12-02 | GOSD05 | V50-39(10) | Routine | WATER SYSTEM (B10) | Building 10 | After EDI (B10) | PW | 2025-12-03 | 2025-12-06 | 0 | 0 | 0 | NA | 100 | PASSED | WA
2025-12-02 | GOSD08 | SV117.01 | Routine | WATER SYSTEM (B10) | Building 10 | Return loop (B10) | PW | 2025-12-03 | 2025-12-06 | 0 | 0 | 0 | NA | 100 | PASSED | WA
2025-12-02 | OSD06 | DV116.18 | Routine | 10-3-111 | Building 10 | WET GRANULATION-5 | PW | 2025-12-03 | 2025-12-06 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-12-02 | OSD07 | DV116.16 | Routine | 10-3-107 | Building 10 | WET GRANULATION-2 | PW | 2025-12-03 | 2025-12-06 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-12-02 | OSD08 | SV116.11 | Routine | 10-3-107 | Building 10 | WET GRANULATION-2 | PW | 2025-12-03 | 2025-12-06 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-12-02 | OSD09 | DV116.14 | Routine | 10-3-086 | Building 10 | TOOL WASHING | PW | 2025-12-03 | 2025-12-06 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-12-02 | OSD10 | SV116.09 | Routine | 10-3-078 | Building 10 | WASHING | PW | 2025-12-03 | 2025-12-06 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-12-02 | OSD11 | DV116.13 | Routine | 10-3-078 | Building 10 | WASHING | PW | 2025-12-03 | 2025-12-06 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-12-02 | OSD27 | DV116.17 | Routine | 10-3-117 | Building 10 | IPQC-2 | PW | 2025-12-03 | 2025-12-06 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-12-02 | OSD28 | DV116.15 | Routine | 10-3-104 | Building 10 | BINDER PREPARATION | PW | 2025-12-03 | 2025-12-06 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-12-12 | GOSD06 | SV113.01 | Routine | WATER SYSTEM (B10) | Building 10 | After Storage tank (B10) | PW | 2025-12-13 | 2025-12-16 | 0 | 0 | 0 | NA | 100 | PASSED | WA
2025-12-12 | GOSD07 | SV115.02 | Routine | WATER SYSTEM (B10) | Building 10 | After UV (B10) | PW | 2025-12-13 | 2025-12-16 | 0 | 0 | 0 | NA | 100 | PASSED | WA
2025-12-12 | GOSD08 | SV117.01 | Routine | WATER SYSTEM (B10) | Building 10 | Return loop (B10) | PW | 2025-12-13 | 2025-12-16 | 0 | 0 | 0 | NA | 100 | PASSED | WA
2025-12-12 | OSD22 | SV116.05 | Routine | 10-3-062 | Building 10 | COATING ROOM-3 | PW | 2025-12-13 | 2025-12-16 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-12-12 | OSD23 | SV116.04 | Routine | 10-3-061 | Building 10 | COATING ROOM-2 | PW | 2025-12-13 | 2025-12-16 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-12-12 | OSD24 | DV116.09 | Routine | 10-3-060 | Building 10 | COATING SOLUTION PREP.-2 | PW | 2025-12-13 | 2025-12-16 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-12-12 | OSD25 | DV116.08 | Routine | 10-3-059 | Building 10 | COATING SOLUTION PREP.-1 | PW | 2025-12-13 | 2025-12-16 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-12-12 | OSD26 | SV116.03 | Routine | 10-3-058 | Building 10 | COATING ROOM-1 | PW | 2025-12-13 | 2025-12-16 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-12-12 | OSD29 | SV116.08 | Routine | 10-3-067 | Building 10 | COATING ROOM-6 | PW | 2025-12-13 | 2025-12-16 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-12-12 | OSD30 | DV116.11 | Routine | 10-3-066 | Building 10 | COATING SOLUTION PREP.-4 | PW | 2025-12-13 | 2025-12-16 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-12-12 | OSD31 | DV116.10 | Routine | 10-3-065 | Building 10 | COATING SOLUTION PREP.-3 | PW | 2025-12-13 | 2025-12-16 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-12-12 | OSD32 | SV116.07 | Routine | 10-3-064 | Building 10 | COATING ROOM-5 | PW | 2025-12-13 | 2025-12-16 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-12-12 | OSD33 | SV116.06 | Routine | 10-3-063 | Building 10 | COATING ROOM-4 | PW | 2025-12-13 | 2025-12-16 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-12-12 | OSD36 | DV116.03 | Routine | 10-2-034 | Building 10 | SAMPLE PREPARATION | PW | 2025-12-13 | 2025-12-16 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-12-12 | OSD37 | DV116.06 | Routine | 10-2-034 | Building 10 | SAMPLE PREPARATION | PW | 2025-12-13 | 2025-12-16 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-12-12 | OSD38 | DV116.07 | Routine | 10-2-032 | Building 10 | GLASS-WARE WASHING | PW | 2025-12-13 | 2025-12-16 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-12-12 | OSD39 | DV116.05 | Routine | 10-2-032 | Building 10 | GLASS-WARE WASHING | PW | 2025-12-13 | 2025-12-16 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-12-12 | OSD40 | DV116.04 | Routine | 10-2-037 | Building 10 | SKID FOR BIN WASHING-1 | PW | 2025-12-13 | 2025-12-16 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-12-15 | GOCL07 | SV125.02 | PQ1-2/OCL | WATER SYSTEM (B16) | Building 16 | After UV (B16) | PW | 2025-12-16 | 2025-12-19 | 0 | 0 | 0 | NA | 100 | PASSED | WA
2025-12-15 | GOCL08 | SV127.01 | PQ1-2/OCL | WATER SYSTEM (B16) | Building 16 | Return loop (B16) | PW | 2025-12-16 | 2025-12-19 | 0 | 0 | 0 | NA | 100 | PASSED | WA
2025-12-15 | OCL01 | DV126.02 | PQ1-2/OCL | 16-1-082 | Building 16 | WASHING | PW | 2025-12-16 | 2025-12-19 | 0 | 0 | 0 | NA | 100 | PASSED | 16
2025-12-15 | OCL02 | DV126.01 | PQ1-2/OCL | 16-1-082 | Building 16 | WASHING | PW | 2025-12-16 | 2025-12-19 | 0 | 0 | 0 | NA | 100 | PASSED | 16
2025-12-15 | OCL03 | SV126.02 | PQ1-2/OCL | 16-1-098 | Building 16 | CIP/SIP (EQUIPMENT REQUIREMENT – 200L) | PW | 2025-12-16 | 2025-12-19 | 0 | 0 | 0 | NA | 100 | PASSED | 16
2025-12-15 | OCL04 | DV126.03 | PQ1-2/OCL | 16-1-098 | Building 16 | CIP/SIP (SINK WASHING) | PW | 2025-12-16 | 2025-12-19 | 0 | 0 | 0 | NA | 100 | PASSED | 16
2025-12-15 | OCL05 | SV126.01 | PQ1-2/OCL | 16-1-092 | Building 16 | LINEN WASHING | PW | 2025-12-16 | 2025-12-19 | 0 | 0 | 0 | NA | 100 | PASSED | 16
2025-12-16 | OCL14 | DV126.11 | PQ1-2/OCL | 16-3-073 | Building 16 | MFG 4 (5000L) | PW | 2025-12-17 | 2025-12-20 | 0 | 0 | 0 | NA | 100 | PASSED | 16
2025-12-16 | OCL17 | SV126.15 | PQ1-2/OCL | 16-3-075 | Building 16 | MFG 5 PROCESS (2000L) | PW | 2025-12-17 | 2025-12-20 | 0 | 0 | 0 | NA | 100 | PASSED | 16
2025-12-16 | OCL21 | DV126.05 | PQ1-2/OCL | 16-3-054 | Building 16 | WASHING | PW | 2025-12-17 | 2025-12-20 | 0 | 0 | 0 | NA | 100 | PASSED | 16
2025-12-16 | OCL13 | SV126.19 | PQ1-2/OCL | 16-3-087 | Building 16 | CIP 2 (EQUIPMENT REQUIREMENT) | PW | 2025-12-17 | 2025-12-20 | 0 | 0 | 0 | NA | 100 | PASSED | 16
2025-12-16 | OCL15 | SV126.14 | PQ1-2/OCL | 16-3-073 | Building 16 | MFG 4 (400L) | PW | 2025-12-17 | 2025-12-20 | 0 | 0 | 0 | NA | 100 | PASSED | 16
2025-12-16 | GOCL07 | SV125.02 | PQ1-2/OCL | WATER SYSTEM (B16) | Building 16 | After UV (B16) | PW | 2025-12-17 | 2025-12-20 | 0 | 0 | 0 | NA | 100 | PASSED | WA
2025-12-16 | GOCL08 | SV127.01 | PQ1-2/OCL | WATER SYSTEM (B16) | Building 16 | Return loop (B16) | PW | 2025-12-17 | 2025-12-20 | 0 | 0 | 0 | NA | 100 | PASSED | WA
2025-12-16 | GOLD06 | SV135.02 | PQ1-2/OLD | WATER SYSTEM (B12) | Building 12 | After UV (B12) | PW | 2025-12-17 | 2025-12-20 | 0 | 0 | 0 | NA | 100 | PASSED | WA
2025-12-16 | GOLD07 | SV137.01 | PQ1-2/OLD | WATER SYSTEM (B12) | Building 12 | Return loop (B12) | PW | 2025-12-17 | 2025-12-20 | 0 | 0 | 0 | NA | 100 | PASSED | WA
2025-12-16 | OLD01 | DV136.17 | PQ1-2/OLD | 12-2-065 | Building 12 | WASHING | PW | 2025-12-17 | 2025-12-20 | 0 | 0 | 0 | NA | 100 | PASSED | 12
2025-12-16 | OLD02 | SV136.16 | PQ1-2/OLD | 12-2-057 | Building 12 | CIP 2 | PW | 2025-12-17 | 2025-12-20 | 0 | 0 | 0 | NA | 100 | PASSED | 12
2025-12-16 | OLD03 | SV136.12 | PQ1-2/OLD | 12-2-036 | Building 12 | CIP 1 | PW | 2025-12-17 | 2025-12-20 | 0 | 0 | 0 | NA | 100 | PASSED | 12
2025-12-16 | OLD04 | SV136.07 | PQ1-2/OLD | 12-2-034 | Building 12 | SYRUP PREPARATION | PW | 2025-12-17 | 2025-12-20 | 0 | 0 | 0 | NA | 100 | PASSED | 12
2025-12-16 | OLD05 | SV136.06 | PQ1-2/OLD | 12-2-034 | Building 12 | SYRUP PREPARATION | PW | 2025-12-17 | 2025-12-20 | 0 | 0 | 0 | NA | 100 | PASSED | 12
2025-12-16 | OLD10 | SV136.15 | PQ1-2/OLD | 12-2-055 | Building 12 | CIP 3 | PW | 2025-12-17 | 2025-12-20 | 0 | 0 | 0 | NA | 100 | PASSED | 12
2025-12-16 | OLD12 | SV136.03 | PQ1-2/OLD | 12-2-032 | Building 12 | CAMPHORATED OPIUM TINCTURE | PW | 2025-12-17 | 2025-12-20 | 0 | 0 | 0 | NA | 100 | PASSED | 12
2025-12-16 | OLD13 | SV136.05 | PQ1-2/OLD | 12-2-032 | Building 12 | CAMPHORATED OPIUM TINCTURE | PW | 2025-12-17 | 2025-12-20 | 0 | 0 | 0 | NA | 100 | PASSED | 12
2025-12-16 | OLD14 | SV136.04 | PQ1-2/OLD | 12-2-030 | Building 12 | OPIUM TINCTURE | PW | 2025-12-17 | 2025-12-20 | 0 | 0 | 0 | NA | 100 | PASSED | 12
2025-12-16 | OLD15 | DV136.02 | PQ1-2/OLD | 12-2-028 | Building 12 | ALCOHOL STORAGE | PW | 2025-12-17 | 2025-12-20 | 0 | 0 | 0 | NA | 100 | PASSED | 12
2025-12-16 | OLD17 | DV136.03 | PQ1-2/OLD | 12-2-053 | Building 12 | IPQC | PW | 2025-12-17 | 2025-12-20 | 0 | 0 | 0 | NA | 100 | PASSED | 12
2025-12-16 | OLD19 | DV136.01 | PQ1-2/OLD | 12-1-035 | Building 12 | SUGAR TRANSFERRING | PW | 2025-12-17 | 2025-12-20 | 0 | 0 | 0 | NA | 100 | PASSED | 12
2025-12-16 | OLD20 | DV136.16 | PQ1-2/OLD | 12-1-064 | Building 12 | WASHING | PW | 2025-12-17 | 2025-12-20 | 0 | 0 | 0 | NA | 100 | PASSED | 12
2025-12-16 | BU19-14 | SV-14 | Routine | PROCESS WATER (B19) | Building 19 | AFTER RO SYSTEM NO.12 SV14 | PRW | 2025-12-17 | 2025-12-20 | 0 | 0 | 0 | NA | 500 | PASSED | PR
2025-12-16 | GOSD01 | VB-05(10) | Routine | WATER SYSTEM (B10) | Building 10 | After Chlorine circulation tank (B10) | PRW | 2025-12-17 | 2025-12-20 | 1 | 0 | 1 | NA | 500 | PASSED | WA
2025-12-16 | GOSD03 | V50-61(10) | Routine | WATER SYSTEM (B10) | Building 10 | After Cartridge filter 5 µm (B10) | PRW | 2025-12-17 | 2025-12-20 | 13 | 1 | 7 | NA | 500 | PASSED | WA
2025-12-16 | GOSD04 | V50-11C(10) | Routine | WATER SYSTEM (B10) | Building 10 | After RO (Before EDI) (B10) | RO water | 2025-12-17 | 2025-12-20 | 0 | 0 | 0 | NA | 100 | PASSED | WA
2025-12-16 | GOSD05 | V50-39(10) | Routine | WATER SYSTEM (B10) | Building 10 | After EDI (B10) | PW | 2025-12-17 | 2025-12-20 | 0 | 0 | 0 | NA | 100 | PASSED | WA
2025-12-16 | GOSD08 | SV117.01 | Routine | WATER SYSTEM (B10) | Building 10 | Return loop (B10) | PW | 2025-12-17 | 2025-12-20 | 0 | 0 | 0 | NA | 100 | PASSED | WA
2025-12-16 | OSD16 | DV116.21 | Routine | 10-3-152 | Building 10 | WASHING-P | PW | 2025-12-17 | 2025-12-20 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-12-16 | OSD17 | DV116.22 | Routine | 10-3-152 | Building 10 | WASHING-P | PW | 2025-12-17 | 2025-12-20 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-12-16 | OSD18 | SV116.13 | Routine | 10-3-152 | Building 10 | WASHING-P | PW | 2025-12-17 | 2025-12-20 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-12-16 | OSD20 | DV116.19 | Routine | 10-3-143 | Building 10 | COATING SOLUTION PREP.-P | PW | 2025-12-17 | 2025-12-20 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-12-16 | OSD19 | DV116.20 | Routine | 10-3-149 | Building 10 | IPQC-1-P | PW | 2025-12-17 | 2025-12-20 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-12-16 | OSD15 | DV116.23 | Routine | 10-3-159 | Building 10 | BINDER PREPARATION-P | PW | 2025-12-17 | 2025-12-20 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-12-16 | OSD42 | DV116.01 | Routine | 10-1-057 | Building 10 | WASHING-P | PW | 2025-12-17 | 2025-12-20 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-12-16 | OSD13 | DV116.25 | Routine | 10-3-171 | Building 10 | TOOL WASHING-P | PW | 2025-12-17 | 2025-12-20 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-12-16 | OSD14 | DV116.24 | Routine | 10-3-163 | Building 10 | WET GRANULATION 1-P | PW | 2025-12-17 | 2025-12-20 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-12-16 | OSD41 | DV116.02 | Routine | 10-1-115 | Building 10 | WASHING | PW | 2025-12-17 | 2025-12-20 | 6 | 3 | 5 |  | 100 | PASSED | 10
2025-12-16 | OSD21 | SV116.12 | Routine | 10-3-144 | Building 10 | COATING-P | PW | 2025-12-17 | 2025-12-20 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-12-17 | OCL08 | DV126.09 | PQ1-2/OCL | 16-3-090 | Building 16 | CIP 1 (ZINK WASHING) | PW | 2025-12-18 | 2025-12-21 | 0 | 0 | 0 | NA | 100 | PASSED | 16
2025-12-17 | OCL07 | SV126.21 | PQ1-2/OCL | 16-3-090 | Building 16 | CIP 1 (EQUIPMENT REQUIREMENT) | PW | 2025-12-18 | 2025-12-21 | 0 | 0 | 0 | NA | 100 | PASSED | 16
2025-12-17 | OCL20 | SV126.05 | PQ1-2/OCL | 16-3-049 | Building 16 | LINEN WASHING | PW | 2025-12-18 | 2025-12-21 | 0 | 0 | 0 | NA | 100 | PASSED | 16
2025-12-17 | OCL06 | SV126.06 | PQ1-2/OCL | 16-3-067 | Building 16 | MFG 1 | PW | 2025-12-18 | 2025-12-21 | 0 | 0 | 0 | NA | 100 | PASSED | 16
2025-12-17 | OCL16 | SV126.18 | PQ1-2/OCL | 16-3-085 | Building 16 | CIP 3 (EQUIPMENT REQUIREMENT) | PW | 2025-12-18 | 2025-12-21 | 0 | 0 | 0 | NA | 100 | PASSED | 16
2025-12-17 | GOCL07 | SV125.02 | PQ1-2/OCL | WATER SYSTEM (B16) | Building 16 | After UV (B16) | PW | 2025-12-18 | 2025-12-21 | 0 | 0 | 0 | NA | 100 | PASSED | WA
2025-12-17 | GOCL08 | SV127.01 | PQ1-2/OCL | WATER SYSTEM (B16) | Building 16 | Return loop (B16) | PW | 2025-12-18 | 2025-12-21 | 0 | 0 | 0 | NA | 100 | PASSED | WA
2025-12-17 | GOLD06 | SV135.02 | PQ1-2/OLD | WATER SYSTEM (B12) | Building 12 | After UV (B12) | PW | 2025-12-18 | 2025-12-21 | 0 | 0 | 0 | NA | 100 | PASSED | WA
2025-12-17 | GOLD07 | SV137.01 | PQ1-2/OLD | WATER SYSTEM (B12) | Building 12 | Return loop (B12) | PW | 2025-12-18 | 2025-12-21 | 0 | 0 | 0 | NA | 100 | PASSED | WA
2025-12-17 | OLD06 | SV136.09 | PQ1-2/OLD | 12-2-039 | Building 12 | MFG 1 | PW | 2025-12-18 | 2025-12-21 | 0 | 0 | 0 | NA | 100 | PASSED | 12
2025-12-17 | OLD07 | SV136.10 | PQ1-2/OLD | 12-2-041 | Building 12 | MFG 2 | PW | 2025-12-18 | 2025-12-21 | 0 | 0 | 0 | NA | 100 | PASSED | 12
2025-12-17 | OLD08 | SV136.11 | PQ1-2/OLD | 12-2-043 | Building 12 | MFG 3 | PW | 2025-12-18 | 2025-12-21 | 0 | 0 | 0 | NA | 100 | PASSED | 12
2025-12-17 | OLD09 | SV136.13 | PQ1-2/OLD | 12-2-043 | Building 12 | MFG 3 | PW | 2025-12-18 | 2025-12-21 | 0 | 0 | 0 | NA | 100 | PASSED | 12
2025-12-17 | OLD11 | SV136.08 | PQ1-2/OLD | 12-2-043 | Building 12 | MFG 3 | PW | 2025-12-18 | 2025-12-21 | 0 | 0 | 0 | NA | 100 | PASSED | 12
2025-12-17 | OLD18 | SV136.02 | PQ1-2/OLD | 12-2-024 | Building 12 | LIQUORICE EXTRACT | PW | 2025-12-18 | 2025-12-21 | 0 | 0 | 0 | NA | 100 | PASSED | 12
2025-12-17 | OLD16 | SV136.14 | PQ1-2/OLD | 12-2-045 | Building 12 | MFG 4 | PW | 2025-12-18 | 2025-12-21 | 0 | 0 | 0 | NA | 100 | PASSED | 12
2025-12-18 | OCL11 | SV126.10 | PQ1-2/OCL | 16-3-071 | Building 16 | MFG 3 (1200L) | PW | 2025-12-19 | 2025-12-22 | 0 | 0 | 0 | NA | 100 | PASSED | 16
2025-12-18 | OCL09 | DV126.10 | PQ1-2/OCL | 16-3-069 | Building 16 | MFG 2 | PW | 2025-12-19 | 2025-12-22 | 0 | 0 | 0 | NA | 100 | PASSED | 16
2025-12-18 | OCL10 | DV126.06 | PQ1-2/OCL | 16-3-069 | Building 16 | MFG 2 | PW | 2025-12-19 | 2025-12-22 | 0 | 0 | 0 | NA | 100 | PASSED | 16
2025-12-18 | OCL12 | SV126.09 | PQ1-2/OCL | 16-3-071 | Building 16 | MFG 3 (5000L) | PW | 2025-12-19 | 2025-12-22 | 0 | 0 | 0 | NA | 100 | PASSED | 16
2025-12-18 | OCL18 | DV126.08 | PQ1-2/OCL | 16-3-077 | Building 16 | MFG 6 | PW | 2025-12-19 | 2025-12-22 | 0 | 0 | 0 | NA | 100 | PASSED | 16
2025-12-18 | OCL19 | DV126.07 | PQ1-2/OCL | 16-3-077 | Building 16 | MFG 6 | PW | 2025-12-19 | 2025-12-22 | 0 | 0 | 0 | NA | 100 | PASSED | 16
2025-12-18 | GOCL07 | SV125.02 | PQ1-2/OCL | WATER SYSTEM (B16) | Building 16 | After UV (B16) | PW | 2025-12-19 | 2025-12-22 | 0 | 0 | 0 | NA | 100 | PASSED | WA
2025-12-18 | GOCL08 | SV127.01 | PQ1-2/OCL | WATER SYSTEM (B16) | Building 16 | Return loop (B16) | PW | 2025-12-19 | 2025-12-22 | 0 | 0 | 0 | NA | 100 | PASSED | WA
2025-12-18 | GOLD06 | SV135.02 | PQ1-2/OLD | WATER SYSTEM (B12) | Building 12 | After UV (B12) | PW | 2025-12-19 | 2025-12-22 | 0 | 0 | 0 | NA | 100 | PASSED | WA
2025-12-18 | GOLD07 | SV137.01 | PQ1-2/OLD | WATER SYSTEM (B12) | Building 12 | Return loop (B12) | PW | 2025-12-19 | 2025-12-22 | 0 | 0 | 0 | NA | 100 | PASSED | WA
2025-12-18 | OLD21 | DV136.15 | PQ1-2/OLD | 12-3-078 | Building 12 | GLASSWARE WASHING 2 | PW | 2025-12-19 | 2025-12-22 | 0 | 0 | 0 | NA | 100 | PASSED | 12
2025-12-18 | OLD22 | DV136.13 | PQ1-2/OLD | 12-3-057 | Building 12 | STERILIZATION | PW | 2025-12-19 | 2025-12-22 | 0 | 0 | 0 | NA | 100 | PASSED | 12
2025-12-18 | OLD23 | SV136.18 | PQ1-2/OLD | 12-3-059 | Building 12 | AUTOCLAVE | PW | 2025-12-19 | 2025-12-22 | 0 | 0 | 0 | NA | 100 | PASSED | 12
2025-12-18 | OLD24 | DV136.11 | PQ1-2/OLD | 12-3-059 | Building 12 | AUTOCLAVE | PW | 2025-12-19 | 2025-12-22 | 0 | 0 | 0 | NA | 100 | PASSED | 12
2025-12-18 | OLD25 | DV136.12 | PQ1-2/OLD | 12-3-056 | Building 12 | MEDIA PREPARATION | PW | 2025-12-19 | 2025-12-22 | 0 | 0 | 0 | NA | 100 | PASSED | 12
2025-12-18 | OLD26 | DV136.10 | PQ1-2/OLD | 12-3-056 | Building 12 | MEDIA PREPARATION | PW | 2025-12-19 | 2025-12-22 | 0 | 0 | 0 | NA | 100 | PASSED | 12
2025-12-18 | OLD27 | DV136.14 | PQ1-2/OLD | 12-3-074 | Building 12 | DECONTAMINATION | PW | 2025-12-19 | 2025-12-22 | 0 | 0 | 0 | NA | 100 | PASSED | 12
2025-12-19 | GOCL01 | VB-05 (16) | PQ1-2/OCL | WATER SYSTEM (B16) | Building 16 | After Chlorine circulation tank (B16) | PRW | 2025-12-20 | 2025-12-23 | 0 | 0 | 0 | NA | 500 | PASSED | WA
2025-12-19 | GOCL02 | V50-61 (16) | PQ1-2/OCL | WATER SYSTEM (B16) | Building 16 | After Cartridge filter 5 µm (B16) | PRW | 2025-12-20 | 2025-12-23 | 0 | 0 | 0 | NA | 500 | PASSED | WA
2025-12-19 | GOCL03 | V50-11C (16) | PQ1-2/OCL | WATER SYSTEM (B16) | Building 16 | After RO (Before EDI) (B16) | RO water | 2025-12-20 | 2025-12-23 | 0 | 0 | 0 | NA | 100 | PASSED | WA
2025-12-19 | GOCL04 | V50-39 (16) | PQ1-2/OCL | WATER SYSTEM (B16) | Building 16 | After EDI (B16) | PW | 2025-12-20 | 2025-12-23 | 0 | 0 | 0 | NA | 100 | PASSED | WA
2025-12-19 | GOCL05 | SV123.01 | PQ1-2/OCL | WATER SYSTEM (B16) | Building 16 | After Storage tank (B16) | PW | 2025-12-20 | 2025-12-23 | 0 | 0 | 0 | NA | 100 | PASSED | WA
2025-12-19 | GOCL07 | SV125.02 | PQ1-2/OCL | WATER SYSTEM (B16) | Building 16 | After UV (B16) | PW | 2025-12-20 | 2025-12-23 | 0 | 0 | 0 | NA | 100 | PASSED | WA
2025-12-19 | GOCL08 | SV127.01 | PQ1-2/OCL | WATER SYSTEM (B16) | Building 16 | Return loop (B16) | PW | 2025-12-20 | 2025-12-23 | 0 | 0 | 0 | NA | 100 | PASSED | WA
2025-12-19 | OCL22 | SV126.03 | PQ1-2/OCL | 16-2-010 | Building 16 | WATER SYSTEM (WFI) | PW | 2025-12-20 | 2025-12-23 | 0 | 0 | 0 | NA | 100 | PASSED | 16
2025-12-19 | OCL23 | SV126.04 | PQ1-2/OCL | 16-2-010 | Building 16 | WATER SYSTEM (PSG) | PW | 2025-12-20 | 2025-12-23 | 0 | 0 | 0 | NA | 100 | PASSED | 16
2025-12-19 | OCL24 | DV126.04 | PQ1-2/OCL | 16-2-010 | Building 16 | WATER SYSTEM (PW) | PW | 2025-12-20 | 2025-12-23 | 0 | 0 | 0 | NA | 100 | PASSED | 16
2025-12-19 | GOLD02 | V50-61 (12) | PQ1-2/OLD | WATER SYSTEM (B12) | Building 12 | After Cartridge filter 5 µm (B12) | PRW | 2025-12-20 | 2025-12-23 | 0 | 0 | 0 | NA | 500 | PASSED | WA
2025-12-19 | GOLD03 | V50-11C (12) | PQ1-2/OLD | WATER SYSTEM (B12) | Building 12 | After RO (Before EDI) (B12) | RO water | 2025-12-20 | 2025-12-23 | 0 | 0 | 0 | NA | 100 | PASSED | WA
2025-12-19 | GOLD04 | V50-39 (12) | PQ1-2/OLD | WATER SYSTEM (B12) | Building 12 | After EDI (B12) | PW | 2025-12-20 | 2025-12-23 | 0 | 0 | 0 | NA | 100 | PASSED | WA
2025-12-19 | GOLD05 | SV133.01 | PQ1-2/OLD | WATER SYSTEM (B12) | Building 12 | After Storage tank (B12) | PW | 2025-12-20 | 2025-12-23 | 0 | 0 | 0 | NA | 100 | PASSED | WA
2025-12-19 | GOLD06 | SV135.02 | PQ1-2/OLD | WATER SYSTEM (B12) | Building 12 | After UV (B12) | PW | 2025-12-20 | 2025-12-23 | 0 | 0 | 0 | NA | 100 | PASSED | WA
2025-12-19 | GOLD07 | SV137.01 | PQ1-2/OLD | WATER SYSTEM (B12) | Building 12 | Return loop (B12) | PW | 2025-12-20 | 2025-12-23 | 0 | 0 | 0 | NA | 100 | PASSED | WA
2025-12-19 | OLD28 | DV136.18 | PQ1-2/OLD | 12-3-037 | Building 12 | GLASSWARE WASHING 1 | PW | 2025-12-20 | 2025-12-23 | 0 | 0 | 0 | NA | 100 | PASSED | 12
2025-12-19 | OLD29 | DV136.05 | PQ1-2/OLD | 12-3-037 | Building 12 | GLASSWARE WASHING 1 | PW | 2025-12-20 | 2025-12-23 | 0 | 0 | 0 | NA | 100 | PASSED | 12
2025-12-19 | OLD30 | DV136.06 | PQ1-2/OLD | 12-3-037 | Building 12 | GLASSWARE WASHING 1 | PW | 2025-12-20 | 2025-12-23 | 0 | 0 | 0 | NA | 100 | PASSED | 12
2025-12-19 | OLD31 | DV136.07 | PQ1-2/OLD | 12-3-039 | Building 12 | INSTRUMENT 7 | PW | 2025-12-20 | 2025-12-23 | 0 | 0 | 0 | NA | 100 | PASSED | 12
2025-12-19 | OLD32 | DV136.08 | PQ1-2/OLD | 12-3-042 | Building 12 | SAMPLE PREPARATION | PW | 2025-12-20 | 2025-12-23 | 0 | 0 | 0 | NA | 100 | PASSED | 12
2025-12-19 | OLD33 | DV136.09 | PQ1-2/OLD | 12-3-042 | Building 12 | SAMPLE PREPARATION | PW | 2025-12-20 | 2025-12-23 | 0 | 0 | 0 | NA | 100 | PASSED | 12
2025-12-19 | OLD34 | DV136.04 | PQ1-2/OLD | 12-2-077 | Building 12 | WATER SYSTEM ROOM | PW | 2025-12-20 | 2025-12-23 | 0 | 0 | 0 | NA | 100 | PASSED | 12
2025-12-22 | GOCL07 | SV125.02 | PQ1-2/OCL | WATER SYSTEM (B16) | Building 16 | After UV (B16) | PW | 2025-12-23 | 2025-12-26 | 0 | 0 | 0 | NA | 100 | PASSED | WA
2025-12-22 | GOCL08 | SV127.01 | PQ1-2/OCL | WATER SYSTEM (B16) | Building 16 | Return loop (B16) | PW | 2025-12-23 | 2025-12-26 | 0 | 0 | 0 | NA | 100 | PASSED | WA
2025-12-22 | OCL06 | SV126.06 | PQ1-2/OCL | 16-3-067 | Building 16 | MFG 1 | PW | 2025-12-23 | 2025-12-26 | 0 | 0 | 0 | NA | 100 | PASSED | 16
2025-12-22 | OCL07 | SV126.21 | PQ1-2/OCL | 16-3-090 | Building 16 | CIP 1 (EQUIPMENT REQUIREMENT) | PW | 2025-12-23 | 2025-12-26 | 0 | 0 | 0 | NA | 100 | PASSED | 16
2025-12-22 | OCL08 | DV126.09 | PQ1-2/OCL | 16-3-090 | Building 16 | CIP 1 (ZINK WASHING) | PW | 2025-12-23 | 2025-12-26 | 0 | 0 | 0 | NA | 100 | PASSED | 16
2025-12-22 | OCL16 | SV126.18 | PQ1-2/OCL | 16-3-085 | Building 16 | CIP 3 (EQUIPMENT REQUIREMENT) | PW | 2025-12-23 | 2025-12-26 | 0 | 0 | 0 | NA | 100 | PASSED | 16
2025-12-22 | OCL20 | SV126.05 | PQ1-2/OCL | 16-3-049 | Building 16 | LINEN WASHING | PW | 2025-12-23 | 2025-12-26 | 0 | 0 | 0 | NA | 100 | PASSED | 16
2025-12-22 | GOLD06 | SV135.02 | PQ1-2/OLD | WATER SYSTEM (B12) | Building 12 | After UV (B12) | PW | 2025-12-23 | 2025-12-26 | 0 | 0 | 0 | NA | 100 | PASSED | WA
2025-12-22 | GOLD07 | SV137.01 | PQ1-2/OLD | WATER SYSTEM (B12) | Building 12 | Return loop (B12) | PW | 2025-12-23 | 2025-12-26 | 0 | 0 | 0 | NA | 100 | PASSED | WA
2025-12-22 | OLD06 | SV136.09 | PQ1-2/OLD | 12-2-039 | Building 12 | MFG 1 | PW | 2025-12-23 | 2025-12-26 | 0 | 0 | 0 | NA | 100 | PASSED | 12
2025-12-22 | OLD07 | SV136.10 | PQ1-2/OLD | 12-2-041 | Building 12 | MFG 2 | PW | 2025-12-23 | 2025-12-26 | 0 | 0 | 0 | NA | 100 | PASSED | 12
2025-12-22 | OLD08 | SV136.11 | PQ1-2/OLD | 12-2-043 | Building 12 | MFG 3 | PW | 2025-12-23 | 2025-12-26 | 0 | 0 | 0 | NA | 100 | PASSED | 12
2025-12-22 | OLD09 | SV136.13 | PQ1-2/OLD | 12-2-043 | Building 12 | MFG 3 | PW | 2025-12-23 | 2025-12-26 | 0 | 0 | 0 | NA | 100 | PASSED | 12
2025-12-22 | OLD11 | SV136.08 | PQ1-2/OLD | 12-2-043 | Building 12 | MFG 3 | PW | 2025-12-23 | 2025-12-26 | 0 | 0 | 0 | NA | 100 | PASSED | 12
2025-12-22 | OLD16 | SV136.14 | PQ1-2/OLD | 12-2-045 | Building 12 | MFG 4 | PW | 2025-12-23 | 2025-12-26 | 0 | 0 | 0 | NA | 100 | PASSED | 12
2025-12-22 | OLD18 | SV136.02 | PQ1-2/OLD | 12-2-024 | Building 12 | LIQUORICE EXTRACT | PW | 2025-12-23 | 2025-12-26 | 0 | 0 | 0 | NA | 100 | PASSED | 12
2025-12-22 | GOSD06 | SV113.01 | Routine | WATER SYSTEM (B10) | Building 10 | After Storage tank (B10) | PW | 2025-12-23 | 2025-12-26 | 0 | 0 | 0 | NA | 100 | PASSED | WA
2025-12-22 | GOSD07 | SV115.02 | Routine | WATER SYSTEM (B10) | Building 10 | After UV (B10) | PW | 2025-12-23 | 2025-12-26 | 0 | 0 | 0 | NA | 100 | PASSED | WA
2025-12-22 | GOSD08 | SV117.01 | Routine | WATER SYSTEM (B10) | Building 10 | Return loop (B10) | PW | 2025-12-23 | 2025-12-26 | 0 | 0 | 0 | NA | 100 | PASSED | WA
2025-12-22 | OSD01 | SV116.15 | Routine | 10-4-012 | Building 10 | CIP SKID-1 FOR BIN WASHING-1 | PW | 2025-12-23 | 2025-12-26 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-12-22 | OSD02 | SV116.16 | Routine | 10-4-012 | Building 10 | WIP SKID-3 FOR GRANULATION POTENT | PW | 2025-12-23 | 2025-12-26 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-12-22 | OSD03 | SV116.17 | Routine | 10-4-012 | Building 10 | CIP SKID-2 FOR BIN WASHING-1 | PW | 2025-12-23 | 2025-12-26 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-12-22 | OSD04 | SV116.18 | Routine | 10-4-012 | Building 10 | WIP SKID-1 FOR GRANULATION NON POTENT | PW | 2025-12-23 | 2025-12-26 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-12-22 | OSD05 | SV116.19 | Routine | 10-4-012 | Building 10 | WIP SKID-2 FOR GRANULATION NON POTENT | PW | 2025-12-23 | 2025-12-26 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-12-22 | OSD34 | SV116.02 | Routine | 10-2-037 | Building 10 | SKID FOR BIN WASHING-2 | PW | 2025-12-23 | 2025-12-26 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-12-22 | OSD35 | SV116.01 | Routine | 10-2-021 | Building 10 | INSTRUMENT-1 | PW | 2025-12-23 | 2025-12-26 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-12-22 | OSD43 | DV116.26 | Routine | 10-4-015 | Building 10 | WATER SYSTEM ROOM | PW | 2025-12-23 | 2025-12-26 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2025-12-23 | GOCL07 | SV125.02 | PQ1-2/OCL | WATER SYSTEM (B16) | Building 16 | After UV (B16) | PW | 2025-12-24 | 2025-12-29 | 0 | 0 | 0 | NA | 100 | PASSED | WA
2025-12-23 | GOCL08 | SV127.01 | PQ1-2/OCL | WATER SYSTEM (B16) | Building 16 | Return loop (B16) | PW | 2025-12-24 | 2025-12-29 | 0 | 0 | 0 | NA | 100 | PASSED | WA
2025-12-23 | GOLD06 | SV135.02 | PQ1-2/OLD | WATER SYSTEM (B12) | Building 12 | After UV (B12) | PW | 2025-12-24 | 2025-12-29 | 0 | 0 | 0 | NA | 100 | PASSED | WA
2025-12-23 | GOLD07 | SV137.01 | PQ1-2/OLD | WATER SYSTEM (B12) | Building 12 | Return loop (B12) | PW | 2025-12-24 | 2025-12-29 | 0 | 0 | 0 | NA | 100 | PASSED | WA
2025-12-23 | OCL01 | DV126.02 | PQ1-2/OCL | 16-1-082 | Building 16 | WASHING | PW | 2025-12-24 | 2025-12-29 | 0 | 0 | 0 | NA | 100 | PASSED | 16
2025-12-23 | OCL02 | DV126.01 | PQ1-2/OCL | 16-1-082 | Building 16 | WASHING | PW | 2025-12-24 | 2025-12-29 | 0 | 0 | 0 | NA | 100 | PASSED | 16
2025-12-23 | OCL03 | SV126.02 | PQ1-2/OCL | 16-1-098 | Building 16 | CIP/SIP (EQUIPMENT REQUIREMENT – 200L) | PW | 2025-12-24 | 2025-12-29 | 0 | 0 | 0 | NA | 100 | PASSED | 16
2025-12-23 | OCL05 | SV126.01 | PQ1-2/OCL | 16-1-092 | Building 16 | LINEN WASHING | PW | 2025-12-24 | 2025-12-29 | 0 | 0 | 0 | NA | 100 | PASSED | 16
2025-12-23 | OCL04 | DV126.03 | PQ1-2/OCL | 16-1-098 | Building 16 | CIP/SIP (SINK WASHING) | PW | 2025-12-24 | 2025-12-29 | 0 | 0 | 0 | NA | 100 | PASSED | 16
2025-12-23 | OLD01 | DV136.17 | PQ1-2/OLD | 12-2-065 | Building 12 | WASHING | PW | 2025-12-24 | 2025-12-29 | 0 | 0 | 0 | NA | 100 | PASSED | 12
2025-12-23 | OLD02 | SV136.16 | PQ1-2/OLD | 12-2-057 | Building 12 | CIP 2 | PW | 2025-12-24 | 2025-12-29 | 0 | 0 | 0 | NA | 100 | PASSED | 12
2025-12-23 | OLD10 | SV136.15 | PQ1-2/OLD | 12-2-055 | Building 12 | CIP 3 | PW | 2025-12-24 | 2025-12-29 | 0 | 0 | 0 | NA | 100 | PASSED | 12
2025-12-23 | OLD17 | DV136.03 | PQ1-2/OLD | 12-2-053 | Building 12 | IPQC | PW | 2025-12-24 | 2025-12-29 | 0 | 0 | 0 | NA | 100 | PASSED | 12
2025-12-23 | OLD19 | DV136.01 | PQ1-2/OLD | 12-1-035 | Building 12 | SUGAR TRANSFERRING | PW | 2025-12-24 | 2025-12-29 | 0 | 0 | 0 | NA | 100 | PASSED | 12
2025-12-23 | OLD20 | DV136.16 | PQ1-2/OLD | 12-1-064 | Building 12 | WASHING | PW | 2025-12-24 | 2025-12-29 | 0 | 0 | 0 | NA | 100 | PASSED | 12
2025-12-24 | GOCL07 | SV125.02 | PQ1-2/OCL | WATER SYSTEM (B16) | Building 16 | After UV (B16) | PW | 2025-12-25 | 2025-12-29 | 0 | 0 | 0 | NA | 100 | PASSED | WA
2025-12-24 | GOCL08 | SV127.01 | PQ1-2/OCL | WATER SYSTEM (B16) | Building 16 | Return loop (B16) | PW | 2025-12-25 | 2025-12-29 | 0 | 0 | 0 | NA | 100 | PASSED | WA
2025-12-24 | GOLD06 | SV135.02 | PQ1-2/OLD | WATER SYSTEM (B12) | Building 12 | After UV (B12) | PW | 2025-12-25 | 2025-12-29 | 0 | 0 | 0 | NA | 100 | PASSED | WA
2025-12-24 | GOLD07 | SV137.01 | PQ1-2/OLD | WATER SYSTEM (B12) | Building 12 | Return loop (B12) | PW | 2025-12-25 | 2025-12-29 | 0 | 0 | 0 | NA | 100 | PASSED | WA
2025-12-24 | OCL13 | SV126.19 | PQ1-2/OCL | 16-3-087 | Building 16 | CIP 2 (EQUIPMENT REQUIREMENT) | PW | 2025-12-25 | 2025-12-29 | 0 | 0 | 0 | NA | 100 | PASSED | 16
2025-12-24 | OCL14 | DV126.11 | PQ1-2/OCL | 16-3-073 | Building 16 | MFG 4 (5000L) | PW | 2025-12-25 | 2025-12-29 | 0 | 0 | 0 | NA | 100 | PASSED | 16
2025-12-24 | OCL15 | SV126.14 | PQ1-2/OCL | 16-3-073 | Building 16 | MFG 4 (400L) | PW | 2025-12-25 | 2025-12-29 | 0 | 0 | 0 | NA | 100 | PASSED | 16
2025-12-24 | OCL17 | SV126.15 | PQ1-2/OCL | 16-3-075 | Building 16 | MFG 5 PROCESS (2000L) | PW | 2025-12-25 | 2025-12-29 | 0 | 0 | 0 | NA | 100 | PASSED | 16
2025-12-24 | OCL21 | DV126.05 | PQ1-2/OCL | 16-3-054 | Building 16 | WASHING | PW | 2025-12-25 | 2025-12-29 | 0 | 0 | 0 | NA | 100 | PASSED | 16
2025-12-24 | OLD03 | SV136.12 | PQ1-2/OLD | 12-2-036 | Building 12 | CIP 1 | PW | 2025-12-25 | 2025-12-29 | 0 | 0 | 0 | NA | 100 | PASSED | 12
2025-12-24 | OLD04 | SV136.07 | PQ1-2/OLD | 12-2-034 | Building 12 | SYRUP PREPARATION | PW | 2025-12-25 | 2025-12-29 | 0 | 0 | 0 | NA | 100 | PASSED | 12
2025-12-24 | OLD05 | SV136.06 | PQ1-2/OLD | 12-2-034 | Building 12 | SYRUP PREPARATION | PW | 2025-12-25 | 2025-12-29 | 0 | 0 | 0 | NA | 100 | PASSED | 12
2025-12-24 | OLD12 | SV136.03 | PQ1-2/OLD | 12-2-032 | Building 12 | CAMPHORATED OPIUM TINCTURE | PW | 2025-12-25 | 2025-12-29 | 0 | 0 | 0 | NA | 100 | PASSED | 12
2025-12-24 | OLD13 | SV136.05 | PQ1-2/OLD | 12-2-032 | Building 12 | CAMPHORATED OPIUM TINCTURE | PW | 2025-12-25 | 2025-12-29 | 0 | 0 | 0 | NA | 100 | PASSED | 12
2025-12-24 | OLD14 | SV136.04 | PQ1-2/OLD | 12-2-030 | Building 12 | OPIUM TINCTURE | PW | 2025-12-25 | 2025-12-29 | 0 | 0 | 0 | NA | 100 | PASSED | 12
2025-12-24 | OLD15 | DV136.02 | PQ1-2/OLD | 12-2-028 | Building 12 | ALCOHOL STORAGE | PW | 2025-12-25 | 2025-12-29 | 0 | 0 | 0 | NA | 100 | PASSED | 12
2025-12-25 | GOCL07 | SV125.02 | PQ1-2/OCL | WATER SYSTEM (B16) | Building 16 | After UV (B16) | PW | 2025-12-26 | 2025-12-29 | 1 | 1 | 1 | NA | 100 | PASSED | WA
2025-12-25 | GOCL08 | SV127.01 | PQ1-2/OCL | WATER SYSTEM (B16) | Building 16 | Return loop (B16) | PW | 2025-12-26 | 2025-12-29 | 0 | 0 | 0 | NA | 100 | PASSED | WA
2025-12-25 | GOLD06 | SV135.02 | PQ1-2/OLD | WATER SYSTEM (B12) | Building 12 | After UV (B12) | PW | 2025-12-26 | 2025-12-29 | 0 | 0 | 0 | NA | 100 | PASSED | WA
2025-12-25 | GOLD07 | SV137.01 | PQ1-2/OLD | WATER SYSTEM (B12) | Building 12 | Return loop (B12) | PW | 2025-12-26 | 2025-12-29 | 0 | 0 | 0 | NA | 100 | PASSED | WA
2025-12-25 | OCL09 | DV126.10 | PQ1-2/OCL | 16-3-069 | Building 16 | MFG 2 | PW | 2025-12-26 | 2025-12-29 | 0 | 0 | 0 | NA | 100 | PASSED | 16
2025-12-25 | OCL10 | DV126.06 | PQ1-2/OCL | 16-3-069 | Building 16 | MFG 2 | PW | 2025-12-26 | 2025-12-29 | 0 | 0 | 0 | NA | 100 | PASSED | 16
2025-12-25 | OCL11 | SV126.10 | PQ1-2/OCL | 16-3-071 | Building 16 | MFG 3 (1200L) | PW | 2025-12-26 | 2025-12-29 | 0 | 0 | 0 | NA | 100 | PASSED | 16
2025-12-25 | OCL12 | SV126.09 | PQ1-2/OCL | 16-3-071 | Building 16 | MFG 3 (5000L) | PW | 2025-12-26 | 2025-12-29 | 0 | 0 | 0 | NA | 100 | PASSED | 16
2025-12-25 | OCL18 | DV126.08 | PQ1-2/OCL | 16-3-077 | Building 16 | MFG 6 | PW | 2025-12-26 | 2025-12-29 | 0 | 0 | 0 | NA | 100 | PASSED | 16
2025-12-25 | OCL19 | DV126.07 | PQ1-2/OCL | 16-3-077 | Building 16 | MFG 6 | PW | 2025-12-26 | 2025-12-29 | 0 | 0 | 0 | NA | 100 | PASSED | 16
2025-12-25 | OLD27 | DV136.14 | PQ1-2/OLD | 12-3-074 | Building 12 | DECONTAMINATION | PW | 2025-12-26 | 2025-12-29 | 0 | 0 | 0 | NA | 100 | PASSED | 12
2025-12-25 | OLD21 | DV136.15 | PQ1-2/OLD | 12-3-078 | Building 12 | GLASSWARE WASHING 2 | PW | 2025-12-26 | 2025-12-29 | 0 | 0 | 0 | NA | 100 | PASSED | 12
2025-12-25 | OLD22 | DV136.13 | PQ1-2/OLD | 12-3-057 | Building 12 | STERILIZATION | PW | 2025-12-26 | 2025-12-29 | 0 | 0 | 0 | NA | 100 | PASSED | 12
2025-12-25 | OLD23 | SV136.18 | PQ1-2/OLD | 12-3-059 | Building 12 | AUTOCLAVE | PW | 2025-12-26 | 2025-12-29 | 0 | 0 | 0 | NA | 100 | PASSED | 12
2025-12-25 | OLD24 | DV136.11 | PQ1-2/OLD | 12-3-059 | Building 12 | AUTOCLAVE | PW | 2025-12-26 | 2025-12-29 | 0 | 0 | 0 | NA | 100 | PASSED | 12
2025-12-25 | OLD25 | DV136.12 | PQ1-2/OLD | 12-3-056 | Building 12 | MEDIA PREPARATION | PW | 2025-12-26 | 2025-12-29 | 0 | 0 | 0 | NA | 100 | PASSED | 12
2025-12-25 | OLD26 | DV136.10 | PQ1-2/OLD | 12-3-056 | Building 12 | MEDIA PREPARATION | PW | 2025-12-26 | 2025-12-29 | 0 | 0 | 0 | NA | 100 | PASSED | 12
2025-12-26 | GOCL01 | VB-05 (16) | PQ1-2/OCL | WATER SYSTEM (B16) | Building 16 | After Chlorine circulation tank (B16) | PRW | 2025-12-27 | 2025-12-30 | 0 | 0 | 0 | NA | 500 | PASSED | WA
2025-12-26 | GOCL02 | V50-61 (16) | PQ1-2/OCL | WATER SYSTEM (B16) | Building 16 | After Cartridge filter 5 µm (B16) | PRW | 2025-12-27 | 2025-12-30 | 0 | 0 | 0 | NA | 500 | PASSED | WA
2025-12-26 | GOCL03 | V50-11C (16) | PQ1-2/OCL | WATER SYSTEM (B16) | Building 16 | After RO (Before EDI) (B16) | RO water | 2025-12-27 | 2025-12-30 | 0 | 0 | 0 | NA | 100 | PASSED | WA
2025-12-26 | GOCL04 | V50-39 (16) | PQ1-2/OCL | WATER SYSTEM (B16) | Building 16 | After EDI (B16) | PW | 2025-12-27 | 2025-12-30 | 0 | 0 | 0 | NA | 100 | PASSED | WA
2025-12-26 | GOCL05 | SV123.01 | PQ1-2/OCL | WATER SYSTEM (B16) | Building 16 | After Storage tank (B16) | PW | 2025-12-27 | 2025-12-30 | 0 | 0 | 0 | NA | 100 | PASSED | WA
2025-12-26 | GOCL07 | SV125.02 | PQ1-2/OCL | WATER SYSTEM (B16) | Building 16 | After UV (B16) | PW | 2025-12-27 | 2025-12-30 | 0 | 0 | 0 | NA | 100 | PASSED | WA
2025-12-26 | GOCL08 | SV127.01 | PQ1-2/OCL | WATER SYSTEM (B16) | Building 16 | Return loop (B16) | PW | 2025-12-27 | 2025-12-30 | 0 | 0 | 0 | NA | 100 | PASSED | WA
2025-12-26 | OCL22 | SV126.03 | PQ1-2/OCL | 16-2-010 | Building 16 | WATER SYSTEM (WFI) | PW | 2025-12-27 | 2025-12-30 | 0 | 0 | 0 | NA | 100 | PASSED | 16
2025-12-26 | OCL23 | SV126.04 | PQ1-2/OCL | 16-2-010 | Building 16 | WATER SYSTEM (PSG) | PW | 2025-12-27 | 2025-12-30 | 0 | 0 | 0 | NA | 100 | PASSED | 16
2025-12-26 | OCL24 | DV126.04 | PQ1-2/OCL | 16-2-010 | Building 16 | WATER SYSTEM (PW) | PW | 2025-12-27 | 2025-12-30 | 0 | 0 | 0 | NA | 100 | PASSED | 16
2025-12-26 | GOLD01 | VB-05 (12) | PQ1-2/OLD | WATER SYSTEM (B12) | Building 12 | After Chlorine circulation tank | PRW | 2025-12-27 | 2025-12-30 | 0 | 0 | 0 | NA | 500 | PASSED | WA
2025-12-26 | GOLD02 | V50-61 (12) | PQ1-2/OLD | WATER SYSTEM (B12) | Building 12 | After Cartridge filter 5 µm (B12) | PRW | 2025-12-27 | 2025-12-30 | 0 | 0 | 0 | NA | 500 | PASSED | WA
2025-12-26 | GOLD03 | V50-11C (12) | PQ1-2/OLD | WATER SYSTEM (B12) | Building 12 | After RO (Before EDI) (B12) | RO water | 2025-12-27 | 2025-12-30 | 0 | 0 | 0 | NA | 100 | PASSED | WA
2025-12-26 | GOLD04 | V50-39 (12) | PQ1-2/OLD | WATER SYSTEM (B12) | Building 12 | After EDI (B12) | PW | 2025-12-27 | 2025-12-30 | 0 | 0 | 0 | NA | 100 | PASSED | WA
2025-12-26 | GOLD05 | SV133.01 | PQ1-2/OLD | WATER SYSTEM (B12) | Building 12 | After Storage tank (B12) | PW | 2025-12-27 | 2025-12-30 | 0 | 0 | 0 | NA | 100 | PASSED | WA
2025-12-26 | GOLD06 | SV135.02 | PQ1-2/OLD | WATER SYSTEM (B12) | Building 12 | After UV (B12) | PW | 2025-12-27 | 2025-12-30 | 0 | 0 | 0 | NA | 100 | PASSED | WA
2025-12-26 | GOLD07 | SV137.01 | PQ1-2/OLD | WATER SYSTEM (B12) | Building 12 | Return loop (B12) | PW | 2025-12-27 | 2025-12-30 | 0 | 0 | 0 | NA | 100 | PASSED | WA
2025-12-26 | OLD28 | DV136.18 | PQ1-2/OLD | 12-3-037 | Building 12 | GLASSWARE WASHING 1 | PW | 2025-12-27 | 2025-12-30 | 0 | 0 | 0 | NA | 100 | PASSED | 12
2025-12-26 | OLD29 | DV136.05 | PQ1-2/OLD | 12-3-037 | Building 12 | GLASSWARE WASHING 1 | PW | 2025-12-27 | 2025-12-30 | 0 | 0 | 0 | NA | 100 | PASSED | 12
2025-12-26 | OLD30 | DV136.06 | PQ1-2/OLD | 12-3-037 | Building 12 | GLASSWARE WASHING 1 | PW | 2025-12-27 | 2025-12-30 | 0 | 0 | 0 | NA | 100 | PASSED | 12
2025-12-26 | OLD31 | DV136.07 | PQ1-2/OLD | 12-3-039 | Building 12 | INSTRUMENT 7 | PW | 2025-12-27 | 2025-12-30 | 0 | 0 | 0 | NA | 100 | PASSED | 12
2025-12-26 | OLD32 | DV136.08 | PQ1-2/OLD | 12-3-042 | Building 12 | SAMPLE PREPARATION | PW | 2025-12-27 | 2025-12-30 | 0 | 0 | 0 | NA | 100 | PASSED | 12
2025-12-26 | OLD33 | DV136.09 | PQ1-2/OLD | 12-3-042 | Building 12 | SAMPLE PREPARATION | PW | 2025-12-27 | 2025-12-30 | 0 | 0 | 0 | NA | 100 | PASSED | 12
2025-12-26 | OLD34 | DV136.04 | PQ1-2/OLD | 12-2-077 | Building 12 | WATER SYSTEM ROOM | PW | 2025-12-27 | 2025-12-30 | 0 | 0 | 0 | NA | 100 | PASSED | 12
2026-01-05 | GWFI01 | V12-4 | Pre PQ3/WFI | 16-2-010 | Building 16 | AFTER WFI GENERATOR | WFI | 2026-01-06 | 2026-01-09 | 0 |  | 0 | NA | 10 | PASSED | 16
2026-01-05 | GWFI02 | SV213.01 | Pre PQ3/WFI | 16-2-010 | Building 16 | AFTER STORAGE TANK | WFI | 2026-01-06 | 2026-01-09 | 0 |  | 0 | NA | 10 | PASSED | 16
2026-01-05 | GWFI03 | SV217.01 | Pre PQ3/WFI | 16-2-010 | Building 16 | RETURN LOOP | WFI | 2026-01-06 | 2026-01-09 | 0 |  | 0 | NA | 10 | PASSED | 16
2026-01-05 | WFI07 | SV216.02 | Pre PQ3/WFI | 16-1-098 | Building 16 | CIP/SIP | WFI | 2026-01-06 | 2026-01-09 | 0 |  | 0 | NA | 10 | PASSED | 16
2026-01-05 | WFI08 | SV216.04 | Pre PQ3/WFI | 16-1-098 | Building 16 | CIP/SIP | WFI | 2026-01-06 | 2026-01-09 | 0 |  | 0 | NA | 10 | PASSED | 16
2026-01-06 | GOLD01 | VB-05 (12) | Routine | WATER SYSTEM (B12) | Building 12 | After Chlorine circulation tank | PRW | 2026-01-07 | 2026-01-10 | 0 | 0 | 0 | NA | 500 | PASSED | WA
2026-01-06 | GOLD02 | V50-61 (12) | Routine | WATER SYSTEM (B12) | Building 12 | After Cartridge filter 5 µm (B12) | PRW | 2026-01-07 | 2026-01-10 | 2 | 2 | 2 | NA | 500 | PASSED | WA
2026-01-06 | GOLD03 | V50-11C (12) | Routine | WATER SYSTEM (B12) | Building 12 | After RO (Before EDI) (B12) | RO water | 2026-01-07 | 2026-01-10 | 0 | 0 | 0 | NA | 100 | PASSED | WA
2026-01-06 | GOLD04 | V50-39 (12) | Routine | WATER SYSTEM (B12) | Building 12 | After EDI (B12) | PW | 2026-01-07 | 2026-01-10 | 0 | 0 | 0 | NA | 100 | PASSED | WA
2026-01-06 | GOLD07 | SV137.01 | Routine | WATER SYSTEM (B12) | Building 12 | Return loop (B12) | PW | 2026-01-07 | 2026-01-10 | 0 | 0 | 0 | NA | 100 | PASSED | WA
2026-01-06 | OLD21 | DV136.15 | Routine | 12-3-078 | Building 12 | GLASSWARE WASHING 2 | PW | 2026-01-07 | 2026-01-10 | 0 | 0 | 0 | NA | 100 | PASSED | 12
2026-01-06 | OLD22 | DV136.13 | Routine | 12-3-057 | Building 12 | STERILIZATION | PW | 2026-01-07 | 2026-01-10 | 0 | 0 | 0 | NA | 100 | PASSED | 12
2026-01-06 | OLD23 | SV136.18 | Routine | 12-3-059 | Building 12 | AUTOCLAVE | PW | 2026-01-07 | 2026-01-10 | 0 | 0 | 0 | NA | 100 | PASSED | 12
2026-01-06 | OLD24 | DV136.11 | Routine | 12-3-059 | Building 12 | AUTOCLAVE | PW | 2026-01-07 | 2026-01-10 | 0 | 0 | 0 | NA | 100 | PASSED | 12
2026-01-06 | OLD25 | DV136.12 | Routine | 12-3-056 | Building 12 | MEDIA PREPARATION | PW | 2026-01-07 | 2026-01-10 | 0 | 0 | 0 | NA | 100 | PASSED | 12
2026-01-06 | OLD26 | DV136.10 | Routine | 12-3-056 | Building 12 | MEDIA PREPARATION | PW | 2026-01-07 | 2026-01-10 | 0 | 0 | 0 | NA | 100 | PASSED | 12
2026-01-06 | OLD27 | DV136.14 | Routine | 12-3-074 | Building 12 | DECONTAMINATION | PW | 2026-01-07 | 2026-01-10 | 0 | 0 | 0 | NA | 100 | PASSED | 12
2026-01-06 | OLD28 | DV136.18 | Routine | 12-3-037 | Building 12 | GLASSWARE WASHING 1 | PW | 2026-01-07 | 2026-01-10 | 0 | 0 | 0 | NA | 100 | PASSED | 12
2026-01-06 | OLD29 | DV136.05 | Routine | 12-3-037 | Building 12 | GLASSWARE WASHING 1 | PW | 2026-01-07 | 2026-01-10 | 0 | 0 | 0 | NA | 100 | PASSED | 12
2026-01-06 | OLD30 | DV136.06 | Routine | 12-3-037 | Building 12 | GLASSWARE WASHING 1 | PW | 2026-01-07 | 2026-01-10 | 0 | 0 | 0 | NA | 100 | PASSED | 12
2026-01-06 | GOCL01 | VB-05 (16) | Routine | WATER SYSTEM (B16) | Building 16 | After Chlorine circulation tank (B16) | PRW | 2026-01-07 | 2026-01-10 | 0 | 0 | 0 | NA | 100 | PASSED | WA
2026-01-06 | GOCL02 | V50-61 (16) | Routine | WATER SYSTEM (B16) | Building 16 | After Cartridge filter 5 µm (B16) | PRW | 2026-01-07 | 2026-01-10 | 111 | 5 | 58 | NA | 100 | PASSED | WA
2026-01-06 | GOCL03 | V50-11C (16) | Routine | WATER SYSTEM (B16) | Building 16 | After RO (Before EDI) (B16) | RO water | 2026-01-07 | 2026-01-10 | 0 | 0 | 0 | NA | 100 | PASSED | WA
2026-01-06 | GOCL04 | V50-39 (16) | Routine | WATER SYSTEM (B16) | Building 16 | After EDI (B16) | PW | 2026-01-07 | 2026-01-10 | 0 | 0 | 0 | NA | 100 | PASSED | WA
2026-01-06 | GOCL08 | SV127.01 | Routine | WATER SYSTEM (B16) | Building 16 | Return loop (B16) | PW | 2026-01-07 | 2026-01-10 | 0 | 0 | 0 | NA | 100 | PASSED | WA
2026-01-06 | OCL01 | DV126.02 | Routine | 16-1-082 | Building 16 | WASHING | PW | 2026-01-07 | 2026-01-10 | 0 | 0 | 0 | NA | 100 | PASSED | 16
2026-01-06 | OCL02 | DV126.01 | Routine | 16-1-082 | Building 16 | WASHING | PW | 2026-01-07 | 2026-01-10 | 0 | 0 | 0 | NA | 100 | PASSED | 16
2026-01-06 | OCL03 | SV126.02 | Routine | 16-1-098 | Building 16 | CIP/SIP (EQUIPMENT REQUIREMENT – 200L) | PW | 2026-01-07 | 2026-01-10 | 0 | 0 | 0 | NA | 100 | PASSED | 16
2026-01-06 | OCL04 | DV126.03 | Routine | 16-1-098 | Building 16 | CIP/SIP (SINK WASHING) | PW | 2026-01-07 | 2026-01-10 | 0 | 0 | 0 | NA | 100 | PASSED | 16
2026-01-06 | OCL05 | SV126.01 | Routine | 16-1-092 | Building 16 | LINEN WASHING | PW | 2026-01-07 | 2026-01-10 | 0 | 0 | 0 | NA | 100 | PASSED | 16
2026-01-06 | OCL22 | SV126.03 | Routine | 16-2-010 | Building 16 | WATER SYSTEM (WFI) | PW | 2026-01-07 | 2026-01-10 | 0 | 0 | 0 | NA | 100 | PASSED | 16
2026-01-06 | GWFI01 | V12-4 | Pre PQ3/WFI | 16-2-010 | Building 16 | AFTER WFI GENERATOR | WFI | 2026-01-08 | 2026-01-12 | 0 |  | 0 | NA | 10 | PASSED | 16
2026-01-06 | GWFI03 | SV217.01 | Pre PQ3/WFI | 16-2-010 | Building 16 | RETURN LOOP | WFI | 2026-01-08 | 2026-01-12 | 0 |  | 0 | NA | 10 | PASSED | 16
2026-01-06 | WFI03 | SV216.03 | Pre PQ3/WFI | 16-1-096 | Building 16 | WASHING/TUNNEL-02 | WFI | 2026-01-08 | 2026-01-12 | 0 |  | 0 | NA | 10 | PASSED | 16
2026-01-06 | WFI04 | POU HE216.03 | Pre PQ3/WFI | 16-1-082 | Building 16 | WASHING | WFI | 2026-01-08 | 2026-01-12 | 0 |  | 0 | NA | 10 | PASSED | 16
2026-01-06 | WFI05 | SV216.06 | Pre PQ3/WFI | 16-1-082 | Building 16 | WASHING | WFI | 2026-01-08 | 2026-01-12 | 0 |  | 0 | NA | 10 | PASSED | 16
2026-01-07 | GWFI01 | V12-4 | Pre PQ3/WFI | 16-2-010 | Building 16 | AFTER WFI GENERATOR | WFI | 2026-01-08 | 2026-01-12 | 0 |  | 0 | NA | 10 | PASSED | 16
2026-01-07 | GWFI03 | SV217.01 | Pre PQ3/WFI | 16-2-010 | Building 16 | RETURN LOOP | WFI | 2026-01-08 | 2026-01-12 | 0 |  | 0 | NA | 10 | PASSED | 16
2026-01-07 | WFI06 | SV216.05 | Pre PQ3/WFI | 16-1-110 | Building 16 | DISINFECTANT PREPARATION | WFI | 2026-01-08 | 2026-01-12 | 0 |  | 0 | NA | 10 | PASSED | 16
2026-01-07 | WFI09 | SV216.10 | Pre PQ3/WFI | 16-1-105 | Building 16 | WASHING/TUNNEL-01 | WFI | 2026-01-08 | 2026-01-12 | 0 |  | 0 | NA | 10 | PASSED | 16
2026-01-08 | GWFI01 | V12-4 | Pre PQ3/WFI | 16-2-010 | Building 16 | AFTER WFI GENERATOR | WFI | 2026-01-10 | 2026-01-13 | 0 |  | 0 | NA | 10 | PASSED | 16
2026-01-08 | GWFI03 | SV217.01 | Pre PQ3/WFI | 16-2-010 | Building 16 | RETURN LOOP | WFI | 2026-01-10 | 2026-01-13 | 0 |  | 0 | NA | 10 | PASSED | 16
2026-01-08 | WFI01 | POU HE216.01 | Pre PQ3/WFI | 16-1-107 | Building 16 | COMPOUNDING-01 | WFI | 2026-01-10 | 2026-01-13 | 0 |  | 0 | NA | 10 | PASSED | 16
2026-01-08 | WFI01 | POU HE216.01 | Pre PQ3/WFI | 16-1-107 | Building 16 | COMPOUNDING-01 | WFI | 2026-01-10 | 2026-01-13 | 0 |  | 0 | ข้างถัง | 10 | PASSED | 16
2026-01-08 | WFI02 | POU HE216.02 | Pre PQ3/WFI | 16-1-107 | Building 16 | COMPOUNDING-01 | WFI | 2026-01-10 | 2026-01-13 | 1 |  | 1 | NA | 10 | PASSED | 16
2026-01-08 | WFI02 | POU HE216.02 | Pre PQ3/WFI | 16-1-107 | Building 16 | COMPOUNDING-01 | WFI | 2026-01-10 | 2026-01-13 | 11 |  | 11 | ข้างถัง | 10 | NOT-PASSED | 16
2026-01-09 | GWFI01 | V12-4 | Pre PQ3/WFI | 16-2-010 | Building 16 | AFTER WFI GENERATOR | WFI | 2026-01-10 | 2026-01-13 | 0 |  | 0 | NA | 10 | PASSED | 16
2026-01-09 | GWFI03 | SV217.01 | Pre PQ3/WFI | 16-2-010 | Building 16 | RETURN LOOP | WFI | 2026-01-10 | 2026-01-13 | 0 |  | 0 | NA | 10 | PASSED | 16
2026-01-09 | WFI10 | POU HE216.04 | Pre PQ3/WFI | 16-1-114 | Building 16 | COMPOUNDING-02 | WFI | 2026-01-10 | 2026-01-13 | 0 |  | 0 | NA | 10 | PASSED | 16
2026-01-09 | WFI10 | POU HE216.04 | Pre PQ3/WFI | 16-1-114 | Building 16 | COMPOUNDING-02 | WFI | 2026-01-10 | 2026-01-13 | 999 |  | 999 | ข้างถัง | 10 | NOT-PASSED | 16
2026-01-09 | WFI11 | POU HE216.05 | Pre PQ3/WFI | 16-1-114 | Building 16 | COMPOUNDING-02 | WFI | 2026-01-10 | 2026-01-13 | 63 |  | 63 | NA | 10 | NOT-PASSED | 16
2026-01-09 | WFI11 | POU HE216.05 | Pre PQ3/WFI | 16-1-114 | Building 16 | COMPOUNDING-02 | WFI | 2026-01-10 | 2026-01-13 | 2 |  | 2 | ข้างถัง | 10 | PASSED | 16
2026-01-09 | BU19-14 | SV-14 | Routine | PROCESS WATER (B19) | Building 19 | AFTER RO SYSTEM NO.12 SV14 | PRW | 2026-01-10 | 2026-01-13 | 0 | 0 | 0 | NA | 500 | PASSED | PR
2026-01-09 | GOSD01 | VB-05(10) | Routine | WATER SYSTEM (B10) | Building 10 | After Chlorine circulation tank (B10) | PRW | 2026-01-10 | 2026-01-13 | 0 | 0 | 0 | NA | 500 | PASSED | WA
2026-01-09 | GOSD03 | V50-61(10) | Routine | WATER SYSTEM (B10) | Building 10 | After Cartridge filter 5 µm (B10) | PRW | 2026-01-10 | 2026-01-13 | 0 | 0 | 0 | NA | 500 | PASSED | WA
2026-01-09 | GOSD04 | V50-11C(10) | Routine | WATER SYSTEM (B10) | Building 10 | After RO (Before EDI) (B10) | RO water | 2026-01-10 | 2026-01-13 | 0 | 0 | 0 | NA | 100 | PASSED | WA
2026-01-09 | GOSD05 | V50-39(10) | Routine | WATER SYSTEM (B10) | Building 10 | After EDI (B10) | PW | 2026-01-10 | 2026-01-13 | 0 | 0 | 0 | NA | 100 | PASSED | WA
2026-01-09 | GOSD08 | SV117.01 | Routine | WATER SYSTEM (B10) | Building 10 | Return loop (B10) | PW | 2026-01-10 | 2026-01-13 | 0 | 0 | 0 | NA | 100 | PASSED | WA
2026-01-09 | OSD06 | DV116.18 | Routine | 10-3-111 | Building 10 | WET GRANULATION-5 | PW | 2026-01-10 | 2026-01-13 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2026-01-09 | OSD07 | DV116.16 | Routine | 10-3-107 | Building 10 | WET GRANULATION-2 | PW | 2026-01-10 | 2026-01-13 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2026-01-09 | OSD08 | SV116.11 | Routine | 10-3-107 | Building 10 | WET GRANULATION-2 | PW | 2026-01-10 | 2026-01-13 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2026-01-09 | OSD09 | DV116.14 | Routine | 10-3-086 | Building 10 | TOOL WASHING | PW | 2026-01-10 | 2026-01-13 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2026-01-09 | OSD10 | SV116.09 | Routine | 10-3-078 | Building 10 | WASHING | PW | 2026-01-10 | 2026-01-13 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2026-01-09 | OSD11 | DV116.13 | Routine | 10-3-078 | Building 10 | WASHING | PW | 2026-01-10 | 2026-01-13 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2026-01-09 | OSD12 | DV116.12 | Routine | 10-3-078 | Building 10 | WASHING | PW | 2026-01-10 | 2026-01-13 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2026-01-09 | OSD27 | DV116.17 | Routine | 10-3-117 | Building 10 | IPQC-2 | PW | 2026-01-10 | 2026-01-13 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2026-01-09 | OSD28 | DV116.15 | Routine | 10-3-104 | Building 10 | BINDER PREPARATION | PW | 2026-01-10 | 2026-01-13 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2026-01-13 | GOCL05 | SV123.01 | Routine | WATER SYSTEM (B16) | Building 16 | After Storage tank (B16) | PW | 2026-01-14 | 2026-01-17 | 0 | 0 | 0 | NA | 100 | PASSED | WA
2026-01-13 | GOCL07 | SV125.02 | Routine | WATER SYSTEM (B16) | Building 16 | After UV (B16) | PW | 2026-01-14 | 2026-01-17 | 0 | 0 | 0 | NA | 100 | PASSED | WA
2026-01-13 | GOCL08 | SV127.01 | Routine | WATER SYSTEM (B16) | Building 16 | Return loop (B16) | PW | 2026-01-14 | 2026-01-17 | 0 | 0 | 0 | NA | 100 | PASSED | WA
2026-01-13 | OCL13 | SV126.19 | Routine | 16-3-087 | Building 16 | CIP 2 (EQUIPMENT REQUIREMENT) | PW | 2026-01-14 | 2026-01-17 | 0 | 0 | 0 | NA | 100 | PASSED | 16
2026-01-13 | OCL14 | DV126.11 | Routine | 16-3-073 | Building 16 | MFG 4 (5000L) | PW | 2026-01-14 | 2026-01-17 | 0 | 0 | 0 | NA | 100 | PASSED | 16
2026-01-13 | OCL15 | SV126.14 | Routine | 16-3-073 | Building 16 | MFG 4 (400L) | PW | 2026-01-14 | 2026-01-17 | 0 | 0 | 0 | NA | 100 | PASSED | 16
2026-01-13 | OCL17 | SV126.15 | Routine | 16-3-075 | Building 16 | MFG 5 PROCESS (2000L) | PW | 2026-01-14 | 2026-01-17 | 0 | 0 | 0 | NA | 100 | PASSED | 16
2026-01-13 | OCL21 | DV126.05 | Routine | 16-3-054 | Building 16 | WASHING | PW | 2026-01-14 | 2026-01-17 | 0 | 0 | 0 | NA | 100 | PASSED | 16
2026-01-13 | OCL23 | SV126.04 | Routine | 16-2-010 | Building 16 | WATER SYSTEM (PSG) | PW | 2026-01-14 | 2026-01-17 | 0 | 0 | 0 | NA | 100 | PASSED | 16
2026-01-13 | GOLD05 | SV133.01 | Routine | WATER SYSTEM (B12) | Building 12 | After Storage tank (B12) | PW | 2026-01-14 | 2026-01-17 | 0 | 0 | 0 | NA | 100 | PASSED | WA
2026-01-13 | GOLD06 | SV135.02 | Routine | WATER SYSTEM (B12) | Building 12 | After UV (B12) | PW | 2026-01-14 | 2026-01-17 | 0 | 0 | 0 | NA | 100 | PASSED | WA
2026-01-13 | GOLD07 | SV137.01 | Routine | WATER SYSTEM (B12) | Building 12 | Return loop (B12) | PW | 2026-01-14 | 2026-01-17 | 0 | 0 | 0 | NA | 100 | PASSED | WA
2026-01-13 | OLD03 | SV136.12 | Routine | 12-2-036 | Building 12 | CIP 1 | PW | 2026-01-14 | 2026-01-17 | 0 | 0 | 0 | NA | 100 | PASSED | 12
2026-01-13 | OLD04 | SV136.07 | Routine | 12-2-034 | Building 12 | SYRUP PREPARATION | PW | 2026-01-14 | 2026-01-17 | 0 | 0 | 0 | NA | 100 | PASSED | 12
2026-01-13 | OLD05 | SV136.06 | Routine | 12-2-034 | Building 12 | SYRUP PREPARATION | PW | 2026-01-14 | 2026-01-17 | 0 | 0 | 0 | NA | 100 | PASSED | 12
2026-01-13 | OLD12 | SV136.03 | Routine | 12-2-032 | Building 12 | CAMPHORATED OPIUM TINCTURE | PW | 2026-01-14 | 2026-01-17 | 0 | 0 | 0 | NA | 100 | PASSED | 12
2026-01-13 | OLD13 | SV136.05 | Routine | 12-2-032 | Building 12 | CAMPHORATED OPIUM TINCTURE | PW | 2026-01-14 | 2026-01-17 | 0 | 0 | 0 | NA | 100 | PASSED | 12
2026-01-13 | OLD14 | SV136.04 | Routine | 12-2-030 | Building 12 | OPIUM TINCTURE | PW | 2026-01-14 | 2026-01-17 | 0 | 0 | 0 | NA | 100 | PASSED | 12
2026-01-13 | OLD15 | DV136.02 | Routine | 12-2-028 | Building 12 | ALCOHOL STORAGE | PW | 2026-01-14 | 2026-01-17 | 0 | 0 | 0 | NA | 100 | PASSED | 12
2026-01-13 | OLD31 | DV136.07 | Routine | 12-3-039 | Building 12 | INSTRUMENT 7 | PW | 2026-01-14 | 2026-01-17 | 0 | 0 | 0 | NA | 100 | PASSED | 12
2026-01-16 | GOSD06 | SV113.01 | Routine | WATER SYSTEM (B10) | Building 10 | After Storage tank (B10) | PW | 2026-01-17 | 2026-01-20 | 0 | 0 | 0 | NA | 100 | PASSED | WA
2026-01-16 | GOSD07 | SV115.02 | Routine | WATER SYSTEM (B10) | Building 10 | After UV (B10) | PW | 2026-01-17 | 2026-01-20 | 0 | 0 | 0 | NA | 100 | PASSED | WA
2026-01-16 | GOSD08 | SV117.01 | Routine | WATER SYSTEM (B10) | Building 10 | Return loop (B10) | PW | 2026-01-17 | 2026-01-20 | 0 | 0 | 0 | NA | 100 | PASSED | WA
2026-01-16 | OSD22 | SV116.05 | Routine | 10-3-062 | Building 10 | COATING ROOM-3 | PW | 2026-01-17 | 2026-01-20 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2026-01-16 | OSD23 | SV116.04 | Routine | 10-3-061 | Building 10 | COATING ROOM-2 | PW | 2026-01-17 | 2026-01-20 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2026-01-16 | OSD24 | DV116.09 | Routine | 10-3-060 | Building 10 | COATING SOLUTION PREP.-2 | PW | 2026-01-17 | 2026-01-20 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2026-01-16 | OSD25 | DV116.08 | Routine | 10-3-059 | Building 10 | COATING SOLUTION PREP.-1 | PW | 2026-01-17 | 2026-01-20 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2026-01-16 | OSD26 | SV116.03 | Routine | 10-3-058 | Building 10 | COATING ROOM-1 | PW | 2026-01-17 | 2026-01-20 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2026-01-16 | OSD29 | SV116.08 | Routine | 10-3-067 | Building 10 | COATING ROOM-6 | PW | 2026-01-17 | 2026-01-20 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2026-01-16 | OSD30 | DV116.11 | Routine | 10-3-066 | Building 10 | COATING SOLUTION PREP.-4 | PW | 2026-01-17 | 2026-01-20 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2026-01-16 | OSD31 | DV116.10 | Routine | 10-3-065 | Building 10 | COATING SOLUTION PREP.-3 | PW | 2026-01-17 | 2026-01-20 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2026-01-16 | OSD32 | SV116.07 | Routine | 10-3-064 | Building 10 | COATING ROOM-5 | PW | 2026-01-17 | 2026-01-20 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2026-01-16 | OSD33 | SV116.06 | Routine | 10-3-063 | Building 10 | COATING ROOM-4 | PW | 2026-01-17 | 2026-01-20 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2026-01-16 | OSD36 | DV116.03 | Routine | 10-2-034 | Building 10 | SAMPLE PREPARATION | PW | 2026-01-17 | 2026-01-20 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2026-01-16 | OSD37 | DV116.06 | Routine | 10-2-034 | Building 10 | SAMPLE PREPARATION | PW | 2026-01-17 | 2026-01-20 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2026-01-16 | OSD38 | DV116.07 | Routine | 10-2-032 | Building 10 | GLASS-WARE WASHING | PW | 2026-01-17 | 2026-01-20 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2026-01-16 | OSD39 | DV116.05 | Routine | 10-2-032 | Building 10 | GLASS-WARE WASHING | PW | 2026-01-17 | 2026-01-20 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2026-01-16 | OSD40 | DV116.04 | Routine | 10-2-037 | Building 10 | SKID FOR BIN WASHING-1 | PW | 2026-01-17 | 2026-01-20 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2026-01-16 | BU11 | #N/A | Routine | #N/A | #N/A | #N/A | #N/A | 2026-01-17 | 2026-01-20 | 0 | 0 | 0 | NA | 100 | PASSED | #N/A
2026-01-19 | GWFI01 | V12-4 | Pre PQ3/WFI | 16-2-010 | Building 16 | AFTER WFI GENERATOR | WFI | 2026-01-20 | 2026-01-23 | 0 |  | 0 | NA | 10 | PASSED | 16
2026-01-19 | GWFI02 | SV213.01 | Pre PQ3/WFI | 16-2-010 | Building 16 | AFTER STORAGE TANK | WFI | 2026-01-20 | 2026-01-23 | 0 |  | 0 | NA | 10 | PASSED | 16
2026-01-19 | GWFI03 | SV217.01 | Pre PQ3/WFI | 16-2-010 | Building 16 | RETURN LOOP | WFI | 2026-01-20 | 2026-01-23 | 0 |  | 0 | NA | 10 | PASSED | 16
2026-01-19 | WFI07 | SV216.02 | Pre PQ3/WFI | 16-1-098 | Building 16 | CIP/SIP | WFI | 2026-01-20 | 2026-01-23 | 0 |  | 0 | NA | 10 | PASSED | 16
2026-01-19 | WFI08 | SV216.04 | Pre PQ3/WFI | 16-1-098 | Building 16 | CIP/SIP | WFI | 2026-01-20 | 2026-01-23 | 0 |  | 0 | NA | 10 | PASSED | 16
2026-01-20 | GOLD01 | VB-05 (12) | Routine | WATER SYSTEM (B12) | Building 12 | After Chlorine circulation tank | PRW | 2026-01-21 | 2026-01-23 | 0 | 0 | 0 | NA | 500 | PASSED | WA
2026-01-20 | GOLD02 | V50-61 (12) | Routine | WATER SYSTEM (B12) | Building 12 | After Cartridge filter 5 µm (B12) | PRW | 2026-01-21 | 2026-01-24 | 0 | 0 | 0 | NA | 500 | PASSED | WA
2026-01-20 | GOLD03 | V50-11C (12) | Routine | WATER SYSTEM (B12) | Building 12 | After RO (Before EDI) (B12) | RO water | 2026-01-21 | 2026-01-24 | 0 | 0 | 0 | NA | 100 | PASSED | WA
2026-01-20 | GOLD04 | V50-39 (12) | Routine | WATER SYSTEM (B12) | Building 12 | After EDI (B12) | PW | 2026-01-21 | 2026-01-24 | 0 | 0 | 0 | NA | 100 | PASSED | WA
2026-01-20 | GOLD07 | SV137.01 | Routine | WATER SYSTEM (B12) | Building 12 | Return loop (B12) | PW | 2026-01-21 | 2026-01-24 | 0 | 0 | 0 | NA | 100 | PASSED | WA
2026-01-20 | OLD01 | DV136.17 | Routine | 12-2-065 | Building 12 | WASHING | PW | 2026-01-21 | 2026-01-24 | 0 | 0 | 0 | NA | 100 | PASSED | 12
2026-01-20 | OLD02 | SV136.16 | Routine | 12-2-057 | Building 12 | CIP 2 | PW | 2026-01-21 | 2026-01-24 | 0 | 0 | 0 | NA | 100 | PASSED | 12
2026-01-20 | OLD10 | SV136.15 | Routine | 12-2-055 | Building 12 | CIP 3 | PW | 2026-01-21 | 2026-01-24 | 0 | 0 | 0 | NA | 100 | PASSED | 12
2026-01-20 | OLD17 | DV136.03 | Routine | 12-2-053 | Building 12 | IPQC | PW | 2026-01-21 | 2026-01-24 | 0 | 0 | 0 | NA | 100 | PASSED | 12
2026-01-20 | OLD19 | DV136.01 | Routine | 12-1-035 | Building 12 | SUGAR TRANSFERRING | PW | 2026-01-21 | 2026-01-24 | 0 | 0 | 0 | NA | 100 | PASSED | 12
2026-01-20 | OLD20 | DV136.16 | Routine | 12-1-064 | Building 12 | WASHING | PW | 2026-01-21 | 2026-01-24 | 0 | 0 | 0 | NA | 100 | PASSED | 12
2026-01-20 | OLD34 | DV136.04 | Routine | 12-2-077 | Building 12 | WATER SYSTEM ROOM | PW | 2026-01-21 | 2026-01-24 | 0 | 0 | 0 | NA | 100 | PASSED | 12
2026-01-20 | GOCL01 | VB-05 (16) | Routine | WATER SYSTEM (B16) | Building 16 | After Chlorine circulation tank (B16) | PRW | 2026-01-21 | 2026-01-24 | 0 | 0 | 0 | NA | 500 | PASSED | WA
2026-01-20 | GOCL02 | V50-61 (16) | Routine | WATER SYSTEM (B16) | Building 16 | After Cartridge filter 5 µm (B16) | PRW | 2026-01-21 | 2026-01-24 | 2 | 2 | 2 | NA | 500 | PASSED | WA
2026-01-20 | GOCL03 | V50-11C (16) | Routine | WATER SYSTEM (B16) | Building 16 | After RO (Before EDI) (B16) | RO water | 2026-01-21 | 2026-01-24 | 0 | 0 | 0 | NA | 100 | PASSED | WA
2026-01-20 | GOCL04 | V50-39 (16) | Routine | WATER SYSTEM (B16) | Building 16 | After EDI (B16) | PW | 2026-01-21 | 2026-01-24 | 0 | 0 | 0 | NA | 100 | PASSED | WA
2026-01-20 | GOCL08 | SV127.01 | Routine | WATER SYSTEM (B16) | Building 16 | Return loop (B16) | PW | 2026-01-21 | 2026-01-24 | 0 | 0 | 0 | NA | 100 | PASSED | WA
2026-01-20 | OCL06 | SV126.06 | Routine | 16-3-067 | Building 16 | MFG 1 | PW | 2026-01-21 | 2026-01-24 | 0 | 0 | 0 | NA | 100 | PASSED | 16
2026-01-20 | OCL07 | SV126.21 | Routine | 16-3-090 | Building 16 | CIP 1 (EQUIPMENT REQUIREMENT) | PW | 2026-01-21 | 2026-01-24 | 0 | 0 | 0 | NA | 100 | PASSED | 16
2026-01-20 | OCL08 | DV126.09 | Routine | 16-3-090 | Building 16 | CIP 1 (ZINK WASHING) | PW | 2026-01-21 | 2026-01-24 | 0 | 0 | 0 | NA | 100 | PASSED | 16
2026-01-20 | OCL16 | SV126.18 | Routine | 16-3-085 | Building 16 | CIP 3 (EQUIPMENT REQUIREMENT) | PW | 2026-01-21 | 2026-01-24 | 0 | 0 | 0 | NA | 100 | PASSED | 16
2026-01-20 | OCL20 | SV126.05 | Routine | 16-3-049 | Building 16 | LINEN WASHING | PW | 2026-01-21 | 2026-01-24 | 0 | 0 | 0 | NA | 100 | PASSED | 16
2026-01-20 | OCL24 | DV126.04 | Routine | 16-2-010 | Building 16 | WATER SYSTEM (PW) | PW | 2026-01-21 | 2026-01-24 | 0 | 0 | 0 | NA | 100 | PASSED | 16
2026-01-20 | GWFI01 | V12-4 | Pre PQ3/WFI | 16-2-010 | Building 16 | AFTER WFI GENERATOR | WFI | 2026-01-22 | 2026-01-25 | 0 |  | 0 | NA | 10 | PASSED | 16
2026-01-20 | GWFI03 | SV217.01 | Pre PQ3/WFI | 16-2-010 | Building 16 | RETURN LOOP | WFI | 2026-01-22 | 2026-01-25 | 0 |  | 0 | NA | 10 | PASSED | 16
2026-01-20 | WFI03 | SV216.03 | Pre PQ3/WFI | 16-1-096 | Building 16 | WASHING/TUNNEL-02 | WFI | 2026-01-22 | 2026-01-25 | 0 |  | 0 | NA | 10 | PASSED | 16
2026-01-20 | WFI04 | POU HE216.03 | Pre PQ3/WFI | 16-1-082 | Building 16 | WASHING | WFI | 2026-01-22 | 2026-01-25 | 0 |  | 0 | NA | 10 | PASSED | 16
2026-01-20 | WFI05 | SV216.06 | Pre PQ3/WFI | 16-1-082 | Building 16 | WASHING | WFI | 2026-01-22 | 2026-01-25 | 0 |  | 0 | NA | 10 | PASSED | 16
2026-01-21 | GWFI01 | V12-4 | Pre PQ3/WFI | 16-2-010 | Building 16 | AFTER WFI GENERATOR | WFI | 2026-01-22 | 2026-01-25 | 0 |  | 0 | NA | 10 | PASSED | 16
2026-01-21 | GWFI03 | SV217.01 | Pre PQ3/WFI | 16-2-010 | Building 16 | RETURN LOOP | WFI | 2026-01-22 | 2026-01-25 | 0 |  | 0 | NA | 10 | PASSED | 16
2026-01-21 | WFI06 | SV216.05 | Pre PQ3/WFI | 16-1-110 | Building 16 | DISINFECTANT PREPARATION | WFI | 2026-01-22 | 2026-01-25 | 0 |  | 0 | NA | 10 | PASSED | 16
2026-01-21 | WFI09 | SV216.10 | Pre PQ3/WFI | 16-1-105 | Building 16 | WASHING/TUNNEL-01 | WFI | 2026-01-22 | 2026-01-25 | 0 |  | 0 | NA | 10 | PASSED | 16
2026-01-22 | BU19-14 | SV-14 | Routine | PROCESS WATER (B19) | Building 19 | AFTER RO SYSTEM NO.12 SV14 | PRW | 2026-01-23 | 2026-01-26 | 0 | 0 | 0 | NA | 100 | PASSED | PR
2026-01-22 | GOSD01 | VB-05(10) | Routine | WATER SYSTEM (B10) | Building 10 | After Chlorine circulation tank (B10) | PRW | 2026-01-23 | 2026-01-26 | 0 | 0 | 0 | NA | 100 | PASSED | WA
2026-01-22 | GOSD02 | V50-60(10) | Routine | WATER SYSTEM (B10) | Building 10 | Before Cartridge filter 5 µm (B10) | PRW | 2026-01-23 | 2026-01-26 | 0 | 0 | 0 | NA | 100 | PASSED | WA
2026-01-22 | GOSD03 | V50-61(10) | Routine | WATER SYSTEM (B10) | Building 10 | After Cartridge filter 5 µm (B10) | PRW | 2026-01-23 | 2026-01-26 | 0 | 0 | 0 | NA | 100 | PASSED | WA
2026-01-22 | GOSD04 | V50-11C(10) | Routine | WATER SYSTEM (B10) | Building 10 | After RO (Before EDI) (B10) | RO water | 2026-01-23 | 2026-01-26 | 0 | 0 | 0 | NA | 100 | PASSED | WA
2026-01-22 | GOSD08 | SV117.01 | Routine | WATER SYSTEM (B10) | Building 10 | Return loop (B10) | PW | 2026-01-23 | 2026-01-26 | 0 | 0 | 0 | NA | 100 | PASSED | WA
2026-01-22 | OSD13 | DV116.25 | Routine | 10-3-171 | Building 10 | TOOL WASHING-P | PW | 2026-01-23 | 2026-01-26 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2026-01-22 | OSD14 | DV116.24 | Routine | 10-3-163 | Building 10 | WET GRANULATION 1-P | PW | 2026-01-23 | 2026-01-26 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2026-01-22 | OSD15 | DV116.23 | Routine | 10-3-159 | Building 10 | BINDER PREPARATION-P | PW | 2026-01-23 | 2026-01-26 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2026-01-22 | OSD16 | DV116.21 | Routine | 10-3-152 | Building 10 | WASHING-P | PW | 2026-01-23 | 2026-01-26 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2026-01-22 | OSD17 | DV116.22 | Routine | 10-3-152 | Building 10 | WASHING-P | PW | 2026-01-23 | 2026-01-26 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2026-01-22 | OSD18 | SV116.13 | Routine | 10-3-152 | Building 10 | WASHING-P | PW | 2026-01-23 | 2026-01-26 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2026-01-22 | OSD19 | DV116.20 | Routine | 10-3-149 | Building 10 | IPQC-1-P | PW | 2026-01-23 | 2026-01-26 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2026-01-22 | OSD20 | DV116.19 | Routine | 10-3-143 | Building 10 | COATING SOLUTION PREP.-P | PW | 2026-01-23 | 2026-01-26 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2026-01-22 | OSD21 | SV116.12 | Routine | 10-3-144 | Building 10 | COATING-P | PW | 2026-01-23 | 2026-01-26 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2026-01-22 | OSD41 | DV116.02 | Routine | 10-1-115 | Building 10 | WASHING | PW | 2026-01-23 | 2026-01-26 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2026-01-22 | OSD42 | DV116.01 | Routine | 10-1-057 | Building 10 | WASHING-P | PW | 2026-01-23 | 2026-01-26 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2026-01-22 | GWFI01 | V12-4 | Pre PQ3/WFI | 16-2-010 | Building 16 | AFTER WFI GENERATOR | WFI | 2026-01-24 | 2026-01-27 | 0 |  | 0 | NA | 10 | PASSED | 16
2026-01-22 | GWFI03 | SV217.01 | Pre PQ3/WFI | 16-2-010 | Building 16 | RETURN LOOP | WFI | 2026-01-24 | 2026-01-27 | 0 |  | 0 | NA | 10 | PASSED | 16
2026-01-22 | WFI01 | POU HE216.01 | Pre PQ3/WFI | 16-1-107 | Building 16 | COMPOUNDING-01 | WFI | 2026-01-24 | 2026-01-27 | 0 |  | 0 | NA | 10 | PASSED | 16
2026-01-22 | WFI01 | POU HE216.01 | Pre PQ3/WFI | 16-1-107 | Building 16 | COMPOUNDING-01 | WFI | 2026-01-24 | 2026-01-27 | 0 |  | 0 | ข้างถัง | 10 | PASSED | 16
2026-01-22 | WFI02 | POU HE216.02 | Pre PQ3/WFI | 16-1-107 | Building 16 | COMPOUNDING-01 | WFI | 2026-01-24 | 2026-01-27 | 0 |  | 0 | NA | 10 | PASSED | 16
2026-01-22 | WFI02 | POU HE216.02 | Pre PQ3/WFI | 16-1-107 | Building 16 | COMPOUNDING-01 | WFI | 2026-01-24 | 2026-01-27 | 22 |  | 22 | ข้างถัง | 10 | NOT-PASSED | 16
2026-01-23 | GWFI01 | V12-4 | Pre PQ3/WFI | 16-2-010 | Building 16 | AFTER WFI GENERATOR | WFI | 2026-01-24 | 2026-01-27 | 0 |  | 0 | NA | 10 | PASSED | 16
2026-01-23 | GWFI03 | SV217.01 | Pre PQ3/WFI | 16-2-010 | Building 16 | RETURN LOOP | WFI | 2026-01-24 | 2026-01-27 | 0 |  | 0 | NA | 10 | PASSED | 16
2026-01-23 | WFI10 | POU HE216.04 | Pre PQ3/WFI | 16-1-114 | Building 16 | COMPOUNDING-02 | WFI | 2026-01-24 | 2026-01-27 | 0 |  | 0 | NA | 10 | PASSED | 16
2026-01-23 | WFI10 | POU HE216.04 | Pre PQ3/WFI | 16-1-114 | Building 16 | COMPOUNDING-02 | WFI | 2026-01-24 | 2026-01-27 | 13 |  | 13 | ข้างถัง | 10 | NOT-PASSED | 16
2026-01-23 | WFI11 | POU HE216.05 | Pre PQ3/WFI | 16-1-114 | Building 16 | COMPOUNDING-02 | WFI | 2026-01-24 | 2026-01-27 | 0 |  | 0 | NA | 10 | PASSED | 16
2026-01-23 | WFI11 | POU HE216.05 | Pre PQ3/WFI | 16-1-114 | Building 16 | COMPOUNDING-02 | WFI | 2026-01-24 | 2026-01-27 | 0 |  | 0 | ข้างถัง | 10 | PASSED | 16
2026-01-27 | GOLD05 | SV133.01 | Routine | WATER SYSTEM (B12) | Building 12 | After Storage tank (B12) | PW | 2026-01-28 | 2026-02-02 | 0 | 0 | 0 | NA | 100 | PASSED | WA
2026-01-27 | GOLD06 | SV135.02 | Routine | WATER SYSTEM (B12) | Building 12 | After UV (B12) | PW | 2026-01-28 | 2026-02-02 | 0 | 0 | 0 | NA | 100 | PASSED | WA
2026-01-27 | GOLD07 | SV137.01 | Routine | WATER SYSTEM (B12) | Building 12 | Return loop (B12) | PW | 2026-01-28 | 2026-02-02 | 0 | 0 | 0 | NA | 100 | PASSED | WA
2026-01-27 | OLD06 | SV136.09 | Routine | 12-2-039 | Building 12 | MFG 1 | PW | 2026-01-28 | 2026-02-02 | 0 | 0 | 0 | NA | 100 | PASSED | 12
2026-01-27 | OLD07 | SV136.10 | Routine | 12-2-041 | Building 12 | MFG 2 | PW | 2026-01-28 | 2026-02-02 | 0 | 0 | 0 | NA | 100 | PASSED | 12
2026-01-27 | OLD08 | SV136.11 | Routine | 12-2-043 | Building 12 | MFG 3 | PW | 2026-01-28 | 2026-02-02 | 0 | 0 | 0 | NA | 100 | PASSED | 12
2026-01-27 | OLD09 | SV136.13 | Routine | 12-2-043 | Building 12 | MFG 3 | PW | 2026-01-28 | 2026-02-02 | 0 | 0 | 0 | NA | 100 | PASSED | 12
2026-01-27 | OLD11 | SV136.08 | Routine | 12-2-043 | Building 12 | MFG 3 | PW | 2026-01-28 | 2026-02-02 | 0 | 0 | 0 | NA | 100 | PASSED | 12
2026-01-27 | OLD16 | SV136.14 | Routine | 12-2-045 | Building 12 | MFG 4 | PW | 2026-01-28 | 2026-02-02 | 0 | 0 | 0 | NA | 100 | PASSED | 12
2026-01-27 | OLD18 | SV136.02 | Routine | 12-2-024 | Building 12 | LIQUORICE EXTRACT | PW | 2026-01-28 | 2026-02-02 | 0 | 0 | 0 | NA | 100 | PASSED | 12
2026-01-27 | OLD32 | DV136.08 | Routine | 12-3-042 | Building 12 | SAMPLE PREPARATION | PW | 2026-01-28 | 2026-02-02 | 0 | 0 | 0 | NA | 100 | PASSED | 12
2026-01-27 | OLD33 | DV136.09 | Routine | 12-3-042 | Building 12 | SAMPLE PREPARATION | PW | 2026-01-28 | 2026-02-02 | 0 | 0 | 0 | NA | 100 | PASSED | 12
2026-01-27 | GOCL05 | SV123.01 | Routine | WATER SYSTEM (B16) | Building 16 | After Storage tank (B16) | PW | 2026-01-28 | 2026-02-02 | 0 | 0 | 0 | NA | 100 | PASSED | WA
2026-01-27 | GOCL07 | SV125.02 | Routine | WATER SYSTEM (B16) | Building 16 | After UV (B16) | PW | 2026-01-28 | 2026-02-02 | 0 | 0 | 0 | NA | 100 | PASSED | WA
2026-01-27 | GOCL08 | SV127.01 | Routine | WATER SYSTEM (B16) | Building 16 | Return loop (B16) | PW | 2026-01-28 | 2026-02-02 | 0 | 0 | 0 | NA | 100 | PASSED | WA
2026-01-27 | OCL09 | DV126.10 | Routine | 16-3-069 | Building 16 | MFG 2 | PW | 2026-01-28 | 2026-02-02 | 1 | 0 | 1 | NA | 100 | PASSED | 16
2026-01-27 | OCL10 | DV126.06 | Routine | 16-3-069 | Building 16 | MFG 2 | PW | 2026-01-28 | 2026-02-02 | 0 | 0 | 0 | NA | 100 | PASSED | 16
2026-01-27 | OCL11 | SV126.10 | Routine | 16-3-071 | Building 16 | MFG 3 (1200L) | PW | 2026-01-28 | 2026-02-02 | 0 | 0 | 0 | NA | 100 | PASSED | 16
2026-01-27 | OCL12 | SV126.09 | Routine | 16-3-071 | Building 16 | MFG 3 (5000L) | PW | 2026-01-28 | 2026-02-02 | 0 | 0 | 0 | NA | 100 | PASSED | 16
2026-01-27 | OCL18 | DV126.08 | Routine | 16-3-077 | Building 16 | MFG 6 | PW | 2026-01-28 | 2026-02-02 | 0 | 0 | 0 | NA | 100 | PASSED | 16
2026-01-27 | OCL19 | DV126.07 | Routine | 16-3-077 | Building 16 | MFG 6 | PW | 2026-01-28 | 2026-02-02 | 0 | 0 | 0 | NA | 100 | PASSED | 16
2026-01-28 | GOSD06 | SV113.01 | Routine | WATER SYSTEM (B10) | Building 10 | After Storage tank (B10) | PW | 2026-01-29 | 2026-02-02 | 0 | 0 | 0 | NA | 100 | PASSED | WA
2026-01-28 | GOSD07 | SV115.02 | Routine | WATER SYSTEM (B10) | Building 10 | After UV (B10) | PW | 2026-01-29 | 2026-02-02 | 0 | 0 | 0 | NA | 100 | PASSED | WA
2026-01-28 | GOSD08 | SV117.01 | Routine | WATER SYSTEM (B10) | Building 10 | Return loop (B10) | PW | 2026-01-29 | 2026-02-02 | 0 | 0 | 0 | NA | 100 | PASSED | WA
2026-01-28 | OSD01 | SV116.15 | Routine | 10-4-012 | Building 10 | CIP SKID-1 FOR BIN WASHING-1 | PW | 2026-01-29 | 2026-02-02 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2026-01-28 | OSD02 | SV116.16 | Routine | 10-4-012 | Building 10 | WIP SKID-3 FOR GRANULATION POTENT | PW | 2026-01-29 | 2026-02-02 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2026-01-28 | OSD03 | SV116.17 | Routine | 10-4-012 | Building 10 | CIP SKID-2 FOR BIN WASHING-1 | PW | 2026-01-29 | 2026-02-02 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2026-01-28 | OSD04 | SV116.18 | Routine | 10-4-012 | Building 10 | WIP SKID-1 FOR GRANULATION NON POTENT | PW | 2026-01-29 | 2026-02-02 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2026-01-28 | OSD05 | SV116.19 | Routine | 10-4-012 | Building 10 | WIP SKID-2 FOR GRANULATION NON POTENT | PW | 2026-01-29 | 2026-02-02 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2026-01-28 | OSD34 | SV116.02 | Routine | 10-2-037 | Building 10 | SKID FOR BIN WASHING-2 | PW | 2026-01-29 | 2026-02-02 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2026-01-28 | OSD35 | SV116.01 | Routine | 10-2-021 | Building 10 | INSTRUMENT-1 | PW | 2026-01-29 | 2026-02-02 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2026-01-28 | OSD43 | DV116.26 | Routine | 10-4-015 | Building 10 | WATER SYSTEM ROOM | PW | 2026-01-29 | 2026-02-02 | 0 | 0 | 0 | NA | 100 | PASSED | 10
2026-02-02 | GWFI01 | V12-4 |  | 16-2-010 | Building 16 | AFTER WFI GENERATOR | WFI | 2026-02-03 | 2026-02-06 | 0 |  | 0 | NA | 10 | PASSED | 16
2026-02-02 | GWFI02 | SV213.01 |  | 16-2-010 | Building 16 | AFTER STORAGE TANK | WFI | 2026-02-03 | 2026-02-06 | 0 |  | 0 | NA | 10 | PASSED | 16
2026-02-02 | GWFI03 | SV217.01 |  | 16-2-010 | Building 16 | RETURN LOOP | WFI | 2026-02-03 | 2026-02-06 | 0 |  | 0 | NA | 10 | PASSED | 16
2026-02-02 | WFI07 | SV216.02 |  | 16-1-098 | Building 16 | CIP/SIP | WFI | 2026-02-03 | 2026-02-06 | 0 |  | 0 | NA | 10 | PASSED | 16
2026-02-02 | WFI08 | SV216.04 |  | 16-1-098 | Building 16 | CIP/SIP | WFI | 2026-02-03 | 2026-02-06 | 0 |  | 0 | NA | 10 | PASSED | 16
2026-02-03 | WFI03 | SV216.03 |  | 16-1-096 | Building 16 | WASHING/TUNNEL-02 | WFI | 2026-02-05 | 2026-02-09 | 0 |  | 0 | NA | 10 | PASSED | 16
2026-02-03 | WFI04 | POU HE216.03 |  | 16-1-082 | Building 16 | WASHING | WFI | 2026-02-05 | 2026-02-09 | 0 |  | 0 | NA | 10 | PASSED | 16
2026-02-03 | WFI05 | SV216.06 |  | 16-1-082 | Building 16 | WASHING | WFI | 2026-02-05 | 2026-02-09 | 0 |  | 0 | NA | 10 | PASSED | 16
2026-02-03 | GOCL01 | VB-05 (16) |  | WATER SYSTEM (B16) | Building 16 | After Chlorine circulation tank (B16) | PRW | 2026-02-04 | 2026-02-07 | 0 | 0 | 0 | NA |  | PASSED | WA
2026-02-03 | GOCL02 | V50-61 (16) |  | WATER SYSTEM (B16) | Building 16 | After Cartridge filter 5 µm (B16) | PRW | 2026-02-04 | 2026-02-07 | 0 | 0 | 0 | NA |  | PASSED | WA
2026-02-03 | GOCL03 | V50-11C (16) |  | WATER SYSTEM (B16) | Building 16 | After RO (Before EDI) (B16) | RO water | 2026-02-04 | 2026-02-07 | 0 | 0 | 0 | NA |  | PASSED | WA
2026-02-03 | GOCL04 | V50-39 (16) |  | WATER SYSTEM (B16) | Building 16 | After EDI (B16) | PW | 2026-02-04 | 2026-02-07 | 0 | 0 | 0 | NA |  | PASSED | WA
2026-02-03 | GOCL08 | SV127.01 |  | WATER SYSTEM (B16) | Building 16 | Return loop (B16) | PW | 2026-02-04 | 2026-02-07 | 0 | 0 | 0 | NA |  | PASSED | WA
2026-02-03 | OCL01 | DV126.02 |  | 16-1-082 | Building 16 | WASHING | PW | 2026-02-04 | 2026-02-07 | 0 | 0 | 0 | NA |  | PASSED | 16
2026-02-03 | OCL02 | DV126.01 |  | 16-1-082 | Building 16 | WASHING | PW | 2026-02-04 | 2026-02-07 | 0 | 0 | 0 | NA |  | PASSED | 16
2026-02-03 | OCL03 | SV126.02 |  | 16-1-098 | Building 16 | CIP/SIP (EQUIPMENT REQUIREMENT – 200L) | PW | 2026-02-04 | 2026-02-07 | 0 | 0 | 0 | NA |  | PASSED | 16
2026-02-03 | OCL04 | DV126.03 |  | 16-1-098 | Building 16 | CIP/SIP (SINK WASHING) | PW | 2026-02-04 | 2026-02-07 | 0 | 0 | 0 | NA |  | PASSED | 16
2026-02-03 | OCL05 | SV126.01 |  | 16-1-092 | Building 16 | LINEN WASHING | PW | 2026-02-04 | 2026-02-07 | 0 | 0 | 0 | NA |  | PASSED | 16
2026-02-03 | OCL22 | SV126.03 |  | 16-2-010 | Building 16 | WATER SYSTEM (WFI) | PW | 2026-02-04 | 2026-02-07 | 0 | 0 | 0 | NA |  | PASSED | 16
2026-02-03 | GOLD01 | VB-05 (12) |  | WATER SYSTEM (B12) | Building 12 | After Chlorine circulation tank | PRW | 2026-02-04 | 2026-02-07 | 0 | 0 | 0 | NA |  | PASSED | WA
2026-02-03 | GOLD02 | V50-61 (12) |  | WATER SYSTEM (B12) | Building 12 | After Cartridge filter 5 µm (B12) | PRW | 2026-02-04 | 2026-02-07 | 15 | 21 | 18 | NA |  | NOT-PASSED | WA
2026-02-03 | GOLD03 | V50-11C (12) |  | WATER SYSTEM (B12) | Building 12 | After RO (Before EDI) (B12) | RO water | 2026-02-04 | 2026-02-07 | 0 | 0 | 0 | NA |  | PASSED | WA
2026-02-03 | GOLD04 | V50-39 (12) |  | WATER SYSTEM (B12) | Building 12 | After EDI (B12) | PW | 2026-02-04 | 2026-02-07 | 0 | 0 | 0 | NA |  | PASSED | WA
2026-02-03 | GOLD07 | SV137.01 |  | WATER SYSTEM (B12) | Building 12 | Return loop (B12) | PW | 2026-02-04 | 2026-02-07 | 0 | 0 | 0 | NA |  | PASSED | WA
2026-02-03 | OLD21 | DV136.15 |  | 12-3-078 | Building 12 | GLASSWARE WASHING 2 | PW | 2026-02-04 | 2026-02-07 | 0 | 0 | 0 | NA |  | PASSED | 12
2026-02-03 | OLD22 | DV136.13 |  | 12-3-057 | Building 12 | STERILIZATION | PW | 2026-02-04 | 2026-02-07 | 0 | 0 | 0 | NA |  | PASSED | 12
2026-02-03 | OLD23 | SV136.18 |  | 12-3-059 | Building 12 | AUTOCLAVE | PW | 2026-02-04 | 2026-02-07 | 0 | 0 | 0 | NA |  | PASSED | 12
2026-02-03 | OLD24 | DV136.11 |  | 12-3-059 | Building 12 | AUTOCLAVE | PW | 2026-02-04 | 2026-02-07 | 0 | 0 | 0 | NA |  | PASSED | 12
2026-02-03 | OLD25 | DV136.12 |  | 12-3-056 | Building 12 | MEDIA PREPARATION | PW | 2026-02-04 | 2026-02-07 | 0 | 0 | 0 | NA |  | PASSED | 12
2026-02-03 | OLD26 | DV136.10 |  | 12-3-056 | Building 12 | MEDIA PREPARATION | PW | 2026-02-04 | 2026-02-07 | 0 | 0 | 0 | NA |  | PASSED | 12
2026-02-03 | OLD27 | DV136.14 |  | 12-3-074 | Building 12 | DECONTAMINATION | PW | 2026-02-04 | 2026-02-07 | 0 | 0 | 0 | NA |  | PASSED | 12
2026-02-03 | OLD28 | DV136.18 |  | 12-3-037 | Building 12 | GLASSWARE WASHING 1 | PW | 2026-02-04 | 2026-02-07 | 0 | 0 | 0 | NA |  | PASSED | 12
2026-02-03 | OLD29 | DV136.05 |  | 12-3-037 | Building 12 | GLASSWARE WASHING 1 | PW | 2026-02-04 | 2026-02-07 | 0 | 0 | 0 | NA |  | PASSED | 12
2026-02-03 | OLD30 | DV136.06 |  | 12-3-037 | Building 12 | GLASSWARE WASHING 1 | PW | 2026-02-04 | 2026-02-07 | 0 | 0 | 0 | NA |  | PASSED | 12
2026-02-04 | WFI09 | SV216.10 |  | 16-1-105 | Building 16 | WASHING/TUNNEL-01 | WFI | 2026-02-05 | 2026-02-09 | 0 |  | 0 | NA | 10 | PASSED | 16
2026-02-04 | WFI10 | POU HE216.04 |  | 16-1-114 | Building 16 | COMPOUNDING-02 | WFI | 2026-02-05 | 2026-02-09 | 0 |  | 0 | NA | 10 | PASSED | 16
2026-02-04 | WFI11 | POU HE216.05 |  | 16-1-114 | Building 16 | COMPOUNDING-02 | WFI | 2026-02-05 | 2026-02-09 | 9 |  | 9 | NA | 10 | PASSED | 16
2026-02-05 | WFI01 | POU HE216.01 |  | 16-1-107 | Building 16 | COMPOUNDING-01 | WFI | 2026-02-07 | 2026-02-10 | 0 |  | 0 | NA | 10 | PASSED | 16
2026-02-05 | WFI02 | POU HE216.02 |  | 16-1-107 | Building 16 | COMPOUNDING-01 | WFI | 2026-02-07 | 2026-02-10 | 0 |  | 0 | NA | 10 | PASSED | 16
2026-02-06 | WFI06 | SV216.05 |  | 16-1-110 | Building 16 | DISINFECTANT PREPARATION | WFI | 2026-02-07 | 2026-02-10 | 0 |  | 0 | NA | 10 | PASSED | 16
2026-02-06 | BU19-14 | SV-14 |  | PROCESS WATER (B19) | Building 19 | AFTER RO SYSTEM NO.12 SV14 | PRW | 2026-02-07 | 2026-02-10 | 0 | 0 | 0 | NA |  | PASSED | PR
2026-02-06 | GOSD01 | VB-05(10) |  | WATER SYSTEM (B10) | Building 10 | After Chlorine circulation tank (B10) | PRW | 2026-02-07 | 2026-02-10 | 0 | 0 | 0 | NA |  | PASSED | WA
2026-02-06 | GOSD03 | V50-61(10) |  | WATER SYSTEM (B10) | Building 10 | After Cartridge filter 5 µm (B10) | PRW | 2026-02-07 | 2026-02-10 | 25 | 12 | 19 | NA |  | NOT-PASSED | WA
2026-02-06 | GOSD04 | V50-11C(10) |  | WATER SYSTEM (B10) | Building 10 | After RO (Before EDI) (B10) | RO water | 2026-02-07 | 2026-02-10 | 0 | 0 | 0 | NA |  | PASSED | WA
2026-02-06 | GOSD05 | V50-39(10) |  | WATER SYSTEM (B10) | Building 10 | After EDI (B10) | PW | 2026-02-07 | 2026-02-10 | 0 | 0 | 0 | NA |  | PASSED | WA
2026-02-06 | GOSD08 | SV117.01 |  | WATER SYSTEM (B10) | Building 10 | Return loop (B10) | PW | 2026-02-07 | 2026-02-10 | 0 | 0 | 0 | NA |  | PASSED | WA
2026-02-06 | OSD06 | DV116.18 |  | 10-3-111 | Building 10 | WET GRANULATION-5 | PW | 2026-02-07 | 2026-02-10 | 0 | 0 | 0 | NA |  | PASSED | 10
2026-02-06 | OSD07 | DV116.16 |  | 10-3-107 | Building 10 | WET GRANULATION-2 | PW | 2026-02-07 | 2026-02-10 | 0 | 0 | 0 | NA |  | PASSED | 10
2026-02-06 | OSD08 | SV116.11 |  | 10-3-107 | Building 10 | WET GRANULATION-2 | PW | 2026-02-07 | 2026-02-10 | 0 | 0 | 0 | NA |  | PASSED | 10
2026-02-06 | OSD09 | DV116.14 |  | 10-3-086 | Building 10 | TOOL WASHING | PW | 2026-02-07 | 2026-02-10 | 0 | 0 | 0 | NA |  | PASSED | 10
2026-02-06 | OSD10 | SV116.09 |  | 10-3-078 | Building 10 | WASHING | PW | 2026-02-07 | 2026-02-10 | 0 | 0 | 0 | NA |  | PASSED | 10
2026-02-06 | OSD11 | DV116.13 |  | 10-3-078 | Building 10 | WASHING | PW | 2026-02-07 | 2026-02-10 | 0 | 0 | 0 | NA |  | PASSED | 10
2026-02-06 | OSD12 | DV116.12 |  | 10-3-078 | Building 10 | WASHING | PW | 2026-02-07 | 2026-02-10 | 0 | 0 | 0 | NA |  | PASSED | 10
2026-02-06 | OSD27 | DV116.17 |  | 10-3-117 | Building 10 | IPQC-2 | PW | 2026-02-07 | 2026-02-10 | 0 | 0 | 0 | NA |  | PASSED | 10
2026-02-06 | OSD28 | DV116.15 |  | 10-3-104 | Building 10 | BINDER PREPARATION | PW | 2026-02-07 | 2026-02-10 | 0 | 0 | 0 | NA |  | PASSED | 10
Formulas:
performedDate = [samplingDate]+1
determinedDate = [performedDate]+3